## Slide 1: Meeting 02.04 – Alexander Skaug’s Master thesis
Title: Control structure for consistent inventory control with moving bottleneck
Contents:
  First present some info about the system I am modelling
  Show some cases/simulations
 2 controllers with different SP

## Slide 2: Meeting 02.04 – Alexander Skaug’s Master thesis
Title: Control structure for consistent inventory control with moving bottleneck
In this presentation: 6 cases/simulations for 3 control structures:
  Split range control
  Generalized split range control
  2 controllers with different setpoints
+ MPC, but needs more work
 2 controllers with different SP

## Slide 3
Nominal point:
- Z0 = 0.4, Z1 = 0.5, Z2 = 0.7, Z3 = 0.6, F0, F1, F2, F3 = 0.16 m^3/min
- h1 = 1 [m], h2 = 1.2 [m], h3 = 0.7 [m]
- Z0 TPM
Tunings:
- TauC = 30 minutes
- Integral time set as average of “ideal tuning” for each MV, average around 54 mins
 “Normal” SRC

## Slide 4
Nominal point:
- Z0 = 0.4, Z1 = 0.5, Z2 = 0.7, Z3 = 0.6, F0, F1, F2, F3 = 0.16 m^3/min
- h1 = 1 [m], h2 = 1.2 [m], h3 = 0.7 [m]
- Z0 TPM
Tunings:
- TauC = 30 minutes
 Generalized SRC

## Slide 5
Nominal point:
- Z0 = 0.4, Z1 = 0.5, Z2 = 0.7, Z3 = 0.6, F0, F1, F2, F3 = 0.16 m^3/min
- h1 = 0.3 [m], h2 = 0.3 [m], h3 = 0.3 [m] low because the TPM is at the inlet
(to have room for increase in production)
- Z0 TPM
- Low setpoints: 0.3 for all tanks, high SP: h1_2 = 1.7 [m], h2_2 = 2.0 [m], h3_2 = 1.1 [m]
Tunings:
- TauC = 8 min (tighter tuning because of SP close to limits)
 2 controllers with different SP

## Slide 6
Comments:
Anti-windup is handled by use of tracking/back-calculation.
Additional logic for SRC and Generalized SRC
- Whenever a certain MV/valve is suddenly set by some other source than the “active” controller, the system sees this and a change is made:
- For SRC: update of internal variable v so the second MV is used immediately
- For Gen. SRC: The active controller gives away the baton/token.
 Generalized SRC

## Slide 7
Cases:
Case 1: Disturbance on Z3 (manual reduction)
Case 2: Case 1 but longer disturbance
Case 3: Move TPM from Z0 to Z3  increase Z0 and Z3 at the same time
Case 4: Disturbance on Z2 (manual reduction)
Case 5: Increase and decrease of Z0
Case 6: Change of setpoints in tank to temporarily increase production
 2 controllers with different SP

## Slide 8: SRC - Disturbance for 60 min: Max flow out of tank 3 is 75% of nominal value: Z3 is reduced from 0.6 to 0.45 manually at t=20, disturbance gone 60 minutes later
Case 1

## Slide 9: Generalized SRC – Dist. for 60 min: Max flow out of tank 3 is 75% of nominal value: Z3 is reduced from 0.6 to 0.45 manually at t=20, disturbance gone 60 minutes later
Case 1

## Slide 10: 2 Controllers – Dist. for 60 min: Max flow out of tank 3 is 75% of nominal value: Z3 is reduced from 0.6 to 0.45 manually at t=20, disturbance gone 60 minutes later
Case 1

## Slide 11: SRC - Disturbance for 180 min: Max flow out of tank 3 is 75% of nominal value: Z3 is reduced from 0.6 to 0.45 manually at t=20, disturbance gone 60 minutes later
Case 2

## Slide 12: Generalized SRC – Dist. for 180 min: Max flow out of tank 3 is 75% of nominal value: Z3 is reduced from 0.6 to 0.45 manually at t=20, disturbance gone 60 minutes later
Case 2

## Slide 13: 2 Controllers – Dist. for 180 min: Max flow out of tank 3 is 75% of nominal value: Z3 is reduced from 0.6 to 0.45 manually at t=20, disturbance gone 60 minutes later
Case 2

## Slide 14: SRC – TPM moved from Z0 to Z3
Case 3

## Slide 15: Generalized SRC – TPM moved from Z0 to Z3
Case 3

## Slide 16: 2 Controllers – TPM moved from Z0 to Z3
Case 3

## Slide 17: SRC – Disturbance on Z2
Case 4

## Slide 18: Generalized SRC – Disturbance on Z2
Case 4

## Slide 19: 2 Controllers – Disturbance on Z2
Case 4

## Slide 20: SRC – Increase and decrease of Z0
Case 5

## Slide 21: Generalized SRC – Increase and decrease of Z0
Case 5

## Slide 22: 2 Controllers – Increase and decrease of Z0
Case 5

## Slide 23: SRC – Increase production by reducing setpoint of level
Case 6

## Slide 24: Generalized SRC – Increase production by reducing setpoint of level
Case 6

## Slide 25: 2 Controllers – Increase production by reducing setpoint of level
Case 6