## Slide 1
Krister Forsman
2015-08-22
Structuring
the Structures

## Slide 2: Control structures – an ad-hoc adventure?
Classical control structures:
  cascade; at least 3 different versions
  feedforward
  ratio control; at least 5 different versions
  valve position control, a.k.a. mid-ranging, input resetting, habituating control; at least 4 different versions
  floating setpoint (VPC on self)
  parallel control (2 MVs, 1 CV)
  conditional control (1 MV, 2 CVs), a.k.a selector control
  split-range
My mission
  Document what’s out there
  Systematic (algorithmic) procedure for selecting a structure
  Pros and cons compared to MPC
  Where are there gaps in the theory?

## Slide 3: Control structures Jeopardy
In a typical text book, or control course, control structures are presented in the “Jeopardy” way: Here is the answer, you come up with the question.
Unfortunately, this is also the case among many practitioners:
  A control solution is suggested before it is even clear what the specifications are

## Slide 4: Some history
Apparently this is an area where application came before theory.
The first textbooks dedicated to process control appear in the 50s.
Feedforward used at least since 1925 [2]
Important contributions by Mason, Shinskey, Balchen and many others.
[1] S. Bennet: A history of control engineering 1930-1955. Inst EE. 1993
[2] N.A. Anderson: Instrumentation for Process Measurement and Control. Chilton, 1964.
[3] A. Ivanoff: Theoretical foundations of the automatic regulation of temperature. J. Institute of Fuel, Vol 7, pp. 117-130, 1934
In spite of the wide [...] application of automatic supervision in engineering
the science of the automatic regulation of temperature is at present in the anomalous position
of having erected a vast practical edifice on negligible theoretical foundations. ([3] 1934)

## Slide 5: “Classical structures”? Scope
What I mean by “classical structures”
  More than one PV and/or more than one MV
  Not just variable pairing
  Not paradigms where a process model is explicitly present in the controller
For example the SISO controller below is not within the scope of this study
+
P
u
y
r
F2
F1
F1

## Slide 6: Borderline case: Floating SP control
C1
r1
P1
u1
y2
y
r2
C2
u2
The structure below (“VPC on self”) does not fall within the definition of “classical control structures”
C1
r1
P1
u1
y
r2
C2
-
-
Equivalent:

## Slide 7: Categories for classification
Most obvious: Number of PVs, CVs and MVs (process variables, controlled vars, manipulated vars)
Reason for using the structure
  1: SISO control could be used
    Would stabilize the process, but a structure can give improved disturbance rejection
    Handle nonlinearity; this can be seen as a sub-category of the previous one
  2: SISO control cannot be used
    Multivariable problem; extra degrees of freedom
    Specifications involve several variables
  MPC can be used for all multivariable problems, of course.
Topological properties, using e.g. graph theoretical tools
  Graph isomorphism
  Fundamental properties
Application based
  1: List of processes (evaporator, ....)
  2: Topology and nonlinearities of process

## Slide 8: Categorization by [PV,CV,MV]
Structure | #PVs | #CVs | #MVs | #Controllers
Cascade control | 2 | 2 | 1 | 2
Feedforward from external signal | 2 | 1 | 1 | 1
Mid-ranging (VPC) | 1 | 2 | 2 | 2
Split-range | 1 | 1 | 2 | 1
Conditional control; Selector control | 2 | 2 | 1 | 2
Parallel control | 1 | 1 | 2 | 2
Ratio control, fixed ratio | 2 | 2 | 2 | 1 or 2
Ratio in cascade | 3 | 3 | 3 | 2 or 3
If two rows have the same list of numbers,
can both structures be used for solving the same problem?
This represents a bottom-up approach:
Instrumentation given, what is possible?

## Slide 9: Categorization by rationale
SISO controller could be used
  Cascade control
  Feedforward
SISO controller cannot be used
  Ratio control
  VPC
  Parallel control
  Split range
By “SISO can be used” I mean:
  Fixed setpoint
  Steady state error =0 after load disturbance

## Slide 10: Example: Pressurized liquid system
PC
V1
FT
FC
V2
FT
FT
High pressure
Thruput manipulator
Fixed flow
Atmos pressure
How do we automatically adjust the flow control valves
so that the share of liquid going to V1 is controlled
Atmos pressure

## Slide 11: “Split ratio control”
PC
V1
FT
FC
V2
FT
FT
High pressure
Atmos pressure
Atmos pressure
FC
+
x
Desired
ratio
PV
SP
OP

## Slide 12: Which is best - MPC or classical structures?
Obviously all classical structures can be captured by MPC in some sense
  Are there any reasons for using classical structures?
Advantages of MPC
  Directly captures the specifications
  One, systematic, procedure for all applications
Disadvantage: If a simple classical structure can solve the problem, the cost for MPC is higher:
  manhours for modeling
  license fees
  maintenance
In some aspects the classical structures may be easier to understand, e.g. robustness: the effect of model errors
There are many applications where it is obvious MPC should be used, because “classical” structure gets too complicated. E.g. when you have many limitations (leading to selector solutions)