## Slide 1: Advanced process control part 2
Sigurd Skogestad
NTNU

## Slide 2: History of automatic process control
1900-1930: On/off control
  Problem: Oscillates
1920s: P-control. Problem:
  Problem: Bias
1930s: I-action
  1935: First commercial PI-controller (Foxboro)
  1939: First commercial PID (Taylor)
1940s: ARC: Cascade control, split range control
1960s: «Optimal control» and Kalman Filter
  1970s: Model predictive control
    1980: Commerical (DMC, Setpoint Co.)
1990s: Artifical intelligence for control
  2020s: second attempt (Machine learning)
ARC = Advanced regulatory control

## Slide 3: QUIZ What are the three most important inventions of process control?
Hint 1: According to Sigurd Skogestad
Hint 2: All were in use around 1940
SOLUTION
PID controller, in particular, I-action
Cascade control
Ratio control

## Slide 4: How design standard ARC elements?
Industrial literature (e.g., Shinskey).
  Many nice ideas. But not systematic. Difficult to understand reasoning
Academia: Very little work
  I feel a little alone

## Slide 5: ARC: Standard Advanced control elements
Each element links a subset of inputs with a subset of outputs. Results in simple local design and tuning
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages).
ARC = advanced reguklatory control

## Slide 6: Constraint switching (because it is optimal at steady state)
CV-CV switching
  Control one CV at a time
MV-MV switching
  Use one MV at a time
MV-CV switching
  MV saturates so must give up CV
  Simple («do nothing»)
  Complex (repairing of loops)
Process
Process
Process
Process

## Slide 7: CV-CV switching: Use selectors (E4) (only* option!)
Many CVs paired with one MV.
But only one CV controlled at a time.
Use: Max or Min selector
Sometimes called “override”
  But this term may be misleading
Selector is generally on MV (compare output from many controllers)
Process
Note: Selectors are logic blocks
>
MAX
=
HS
=
<
MIN
=
LS
=
*Not quite true: Selectors may be implemented in other ways, for example, using «if-then»-logic.

## Slide 8: Implementation selector
Alt. I (General). Several controllers (different CVs)
    Selector on MVs
      Must have anti windup for C1 and C2 !
Alt. II (Less general) Controllers in cascade
    Selector on CV setpoint
    Good alternative if CVs (y1 and y2) are related so that cascade is good
    In this case: Selector may be replaced by saturation element
    (with y2s as the max or min)
Alt. III (For special case where all CVs have same bound). One controller
    Selector is on CVs (Auctioneering)
    Also assumes that dynamics from u to y1 and y2 are similar; otherwise use Alt.I
    Example: Control hot-spot in reactor or furnace.
>
y1
y2
y=max(y1,y2)
c
u
ys
Process
u
y1
y2
…
u=max(u0,u1,u2)

## Slide 9: Example Alt. III
Hot-spot control in reactor or furnace
>
T1
T2
.
.
.
Tn
y=max(Ti)
C
u=Q
Comment: Could use General Alternative I (many controllers) for hot-spot control, with each temperature controller (c1, c2,…) computing the heat input (u1=Q1, u2=Q2, ….) and then select u = min(u1, u2, …), but it is more complicated.
CV-CV switching

## Slide 10: Furnace control
TC
u=Fuel gas
Flue gas
Process fluid (water)
Air
T1s = 500C
TC
T2max=700C
y1=T1
u1
u2
u=min(u1,u2)
Input (MV)
u = Fuel gas flowrate
Output (CV)
y1 = process temperature T1
(desired setpoint or max constraint)
y2 = furnace temperature T2
(max constraint)
Rule: Use min-selector for constraints that are satisfied with a small input
CV-CV switching
u = input = manipulated variable (MV)
y = output = controlled variable (CV)
MIN
with safety constraint (Alt. I)
y2=T2
HP steam

## Slide 11: Furnace control with cascade (Alt. II, selector on CV-sp)
TC
u=Fuel gas
Flue gas
Process fluid
Air
T1s = 500C
TC
T2max = 700C
MIN
y1=T1
y2=T2
u1
u2
CV-CV switching, alternative solution
T2s
Comparison
The cascade solution is less general but it may be better in this case.
Why better? Inner T2-loop is fast and always active and may improve control of T1.
Comment: For both Alt. I and II, we loose control of T1 (it drops below T1s=500C) when T2=T2max. If this is not acceptable then we need to something- More on this later!

## Slide 12: Example Alt. I (Choke valve)
The choke valve is normally fully open to avoid unnecessary pressure drop (normally, we may have p1=4.5 bar, p2=4 bar)
But may close choke valve to avoid too low p1 (if N2 supply stops) or too high p2 (if p1 is high).
Here Alt. II (cascade) should not be used (Why? Cascade control makes it necessary to have one loop slow, which makes little sense since control of p1 does not improve control of p2 (or vice-versa).
Comment 1: Strictly speaking. the input u0=100% to the min-block is not needed, since the valve has a “bulit-in” min-selector at fully open (see later). But including it is not wrong - and it shows more clearly that we normally want u0=100%.
Comment 2: There may be quite a lot of interaction between the pressure and flow control. The best solution is probably to make one fast and one slow. In this case, it seems most reasonable to make the pressure control fast. But if fast flow control is needed, we may do it opposite.
Comment 3: I here use the term “choke valve” when the aim is to regulate pressure; and “control valve” when it is to regulate flow (but other people may not agree on this)
CV-CV switching

## Slide 13: Design of selector structure
Rule 1 (max or min selector)
Use max-selector for constraints that are satisfied with a large input
Use min-selector for constraints that are satisfied with a small input
Rule 2 (order of max and min selectors):
If need both max and min selector: Potential infeasibility (conflict)
Order does not matter if problem is feasible
If infeasible: Put highest priority constraint at the end
CV-CV switching
“Systematic design of active constraint switching using selectors.” Dinesh Krishnamoorthy , Sigurd Skogestad. Computers & Chemical Engineering, Volume 143, (2020)
“Advanced control using decomposition and simple elements”. Sigurd Skogestad. Annual Reviews in Control, Volume 56, 100903 (2023)

## Slide 14: Example. Maximize flow with pressure constraints
Op
Input u = z1
Want to maximize flow, J=-F:
CV-CV switching
The two p1-constraints are not conflicting, because they are on the same variable.
However the Fmax-constraint and p1min-constraint may be conflicting: Must choose which is most important.

## Slide 15
Disturbances in p0 and p2 (unmeasured)
CV-CV switching

## Slide 16
t>1800: u=zmax=1
CV-CV switching

## Slide 17: Valves have “built-in” selectors
Rule 3 (a bit opposite of what you may guess)
  A closed valve (umin=0) gives a “built-in” max-selector (to avoid negative flow)
  An open valve (umax=1) gives a “built-in” min-selector
  So: Not necessary to add these as selector blocks (but it will not be wrong).
  The “built-in” selectors are never conflicting because cannot have closed and open at the same time
  Another way to see this is to note that a valve works as a saturation element
CV-CV switching
Saturation element may be implemented in three other ways (equivalent because never conflict)
Min-selector followed by max-selector
Max-selector followed by min-selector
Mid-selector
“Advanced control using decomposition and simple elements”. Sigurd Skogestad. Annual Reviews in Control, Volume 56, 100903 (2023)

## Slide 18: Quiz. Is this OK?
Cristina: I am looking at a control solution using selectors for keeping the pressure within constraints, while maximizing the valve opening. See figure This is for the valve before a steam turbine. This should work OK, right? Of course, if pmax is reached while the valve is fully open, the turbine bypass will have to open.
Answer:
Rule 1. Yes, the rule is to use a max-selector for a constraint which is satisfied with a large input.
And since the pressure is measured upstream, the pressure will get lower if we increase the valve opening, making it easier to satisfy the pmax-constraint. So yes, this is OK.
Rule 1. Similar for the min-block with pmin.
Rule 2. Since you have two constraints on the same variable, you cannot have infeasibility so the order of the min. and max-blocks doesn’t matter for pmin and pmax.
Rule 2. Yes, the desired value uo=zmax should always enter the first block.
Conclusion: yes, it works.
BUT….
Comment 1: But note that there is also a “hidden” min-selector just before the valve because of the valve which has zmax. And also a “hidden” max-selector because of zmin (a fully closed valve). These constraints may be inconsistent with the pressure constraints.
Comment 2: Since the order of the two selectors does not matter in this case, one may instead use the “equivalent” alternative with the max-block first. But we then see clearly that the constraint on pmax will never be activated, because ztmax is large. I guess this makes sense since you want to have the valve as open as possible, so then the you will always be at the pmin-constraint or have a fully open valve. So you can cut the pmax-constraint (and thus the max-selector) as you anyway want to open the valve as much as possible.
In addition, you can also cut the min-selector because there is already a “hidden” min-selector with zmax. (On the other hand, it will not be wrong to keep them.)
CV-CV switching
Final conclusion: Yes, it works, but it’s much too complicated.
All what is shown can be replaced by a pressure controller (PC) with setpoint pmin.

## Slide 19: MV-MV switching
Need several MVs to cover whole steady-state range (because primary MV may saturate)*
Note that we only want to use one MV at the time.
Three solutions:
  Alt.1 Split-range control (one controller) (E5)
  Alt.2 Several controllers with different setpoints (E6)
  Alt.3 Valve position control (E7)
Which is best? It depends on the case!
*Optimal Operation with Changing Active Constraint Regions using Classical Advanced Control, Adriana Reyes-Lua Cristina Zotica, Sigurd Skogestad, Adchem Conference, Shenyang, China. July 2018 ,
Process

## Slide 20: Example MV-MV switching
Break and gas pedal in a car
Use only one at a time
MV-MV switching

## Slide 21: E5. Split-range control (SRC) (for MV-MV switching)
For MVs (u) that have same effect (same sign) on the output (y) (Fig. 21), we need to define the order in which the MVs will be used. This is done by the order in in the SR-block.
Example: With two heating sources, we need to decide which to use first (see next Example)
Advantage: SRC is easy to understand and implement!
Disadvantages:
Only one controller C Same integral time for all inputs ui (MVs)
  Controller gains can be adjusted with slopes in SR-block!
Does not work well for cases where constraint values for ui change
MV-MV switching- Alternative 1.

## Slide 22
MVs (two for summer and two for winter):
AC (expensive cooling)
CW (cooling water, cheap)
HW (hot water, quite cheap)
Electric heat, EH (expensive)
y=T
Alt. 1 Split-range control (SRC)
Example: Room heating with one CV (T) and 4 MVs
MV-MV switching
Note: may adjust the location of split (x-axis) to make loop gains equal.
Disadvantage SRC: 1. Must use same integral time for all MVs
2. Does not work well for cases where constraint values change

## Slide 23
Alt. 1 Simulation Split-range control (SRC).
MV-MV switching

## Slide 24: E6. Separate controllers with different setpoints
MV-MV switching- Alternative 2.
Advantages E6 (compared to split range control, E5):
Simple to implement (no logic)
Controllers can be tuned independently (different integral times)
Switching by feedback: Do not need to know constraint values
  Big advantage when switching point varies (complex MV-CV switching)
Disadvantages:
Temporary loose control during switching
Setpoint not constant
  Can be an advantage (for example, may give energy savings for room heating)

## Slide 25
MVs (two for summer and two for winter):
AC (expensive cooling)
CW (cooling water, cheap)
HW (hot water, quite cheap)
Electric heat, EH (expensive)
y=T
Alt. 2 for MV-MV switching. Multiple controllers with different setpoints
Example: Room heating with one CV (T) and 4 MVs
E6: MV-MV switching, Alt. 2
Disadvantage (comfort):
Different setpoints
Loose control during transition
Advantage (economics) :
Different setpoints (energy savings)
C1
C2
C3
C4
23oC
22oC
21oC
20oC

## Slide 26
A Reyes-Lua, S Skogestad. Multiple-Input Single-Output Control for Extending the Steady-State Operating Range - Use of Controllers with Different Setpoints. Processes 7 (12), 941
y=T
1
3
2
4
d=Tamb

## Slide 27: E7. VPC on main steady-state input
MV-MV switching- Alternative 3.
VPC
Advantages E7 (for MV-MV switching): Always use u1 to control y
  For example, u2 may only allow discrete changes (e.g., u2=0,1,2,3)
  or dynamics for u2 may be very slow
Disadvantages E7:
We cannot let u1 become fully saturated because then control of y is lost
  This means that we cannot use the full range for u1 (potential economic loss)
Related: When u2 is used, we need to keep using a ‘‘little’’ of u1.
  Example: May need to use both heating and cooling at the same time (when u1 normally should be off).

## Slide 28: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=0.9 bar
=1 bar
=1.1 bar
=1 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q = z1
but if Q=0 (because of too hot feed) we must use MV3=vent =z3
and if Q=max (becase of too cold feed) we must use MV2=inert = z2
Alt.3: VPC (z2 and z3 could here be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q=0 (z1=0.1)
Use inert (z2) to avoid Q=max (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
Example: Heating water with intermediate storage. «Inert» could be HP steam.
MV-MV switching
Example: Heating water to 213C = Control steam pressure at 20 bar*.
«Inert» (z2) could be HP steam.
Hot water
Hotter water
* Rule of thumb: p[bar] = [T[C]/100]^4

## Slide 29: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=0.9 bar
=1 bar
=1.1 bar
=20 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q
but if Q=0 we must use MV3=vent
and if Q=max we must use MV2=inert
Alt.3: VPC (z2 and z3 could here be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q=0 (z1=0.1)
Use inert (z2) to avoid Q=max (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
MV-MV switching
Hotter water
Hot water

## Slide 30: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=19 bar
=20 bar
=21 bar
=20 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q
but if Q=0 we must use MV3=vent
and if Q=max we must use MV2=inert
Alt.3: VPC (z2 and z3 could here be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q=0 (z1=0.1)
Use inert (z2) to avoid Q=max (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
MV-MV switching
Hotter water
Hot water

## Slide 31: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=21 bar
=20 bar
=21 bar
=20 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q
but if Q=0 we must use MV3=vent
and if Q=max we must use MV2=inert
Alt.3: VPC (z2 and z3 could here even be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q small (z1=0.1)
Use inert (z2) to avoid Q large (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
MV-MV switching
=20 bar
Hotter water
Hot water

## Slide 32: Beware: Two different applications of VPC (E3 and E7)
The VPC schemes in Figure 12 (E3 - VPC on dynamic input) and Figure 24 (E7) seem to be the same
But their behavior is very different!
  In Figure 12 (E3) both inputs are used all the time
    u1 is used to improve the dynamic response
  In Figure 24 (E7)
    u1 is the main input (and used all the time)
    u2 is only used when u1 approaches saturation (for MV-MV switching)
E3 (Fig. 12)
E7 (Fig. 24)

## Slide 33: Beware: Two different applications of VPC (E3 and E7)
The VPC schemes in Figure 12 (E3 - VPC on dynamic input) and Figure 24 (E7) seem to be the same
  In fact, they are the same - except for the blue saturation elements - which tells that in Figure 24 (E7) the saturation has to be there for the structure to work as expected
But their behavior is very different!
  In Figure 12 (E3) both inputs are used all the time
    u1 is used to improve the dynamic response
    u2 is the main steady-state input (and used all the time)
    u1s is typically 50% (mid-range)
  In Figure 24 (E7)
    u1 is the main input (and used all the time)
    u2 is only used when u1 approaches saturation (for MV-MV switching)
    The setpoint u1s is typically close to the expected saturation constraint (10% or 90%)
I frequently see people confuse these two elements -
which is very understandable!
E3 (Fig. 12)
E7 (Fig. 24)

## Slide 34: Example adaptive cruise control: CV-CV switch followed by MV-MV switch
Note: This is not Complex MV-CV switching, because then the order would be opposite.

## Slide 35: Summary MV-MV switching
Need several MVs to cover whole steady-state range (because primary MV may saturate)*
Note that we only want to use one MV at the time.
  Alt.1 Split-range control (one controller) (E5)
    Advantage: Easy to understand because SR-block shows clearly sequence of MVs
    Disdvantages: (1) Need same tunings (integral time) for all MVs . (2) May not work well if MV-limits inside SR-block change with time, so: Not good for MV-CV switching
  Alt.2 Several controllers with different setpoints (E6)
    Advantages: 1. Simple to implement, do not need to keep track of MVs. 2. Can have independent tunings. .
    Disadvantage: Setpoint varies (which can be turned into an advantage in some cases)
  Alt.3 Valve position control (E7)
    Advantage: Always use “primary” MV for control of CV (avoids repairing of loops)
    Disadvantages: Gives some loss, because primary MV always must be used (cannot go to zero).
Which is best? It depends on the case!
*Optimal Operation with Changing Active Constraint Regions using Classical Advanced Control, Adriana Reyes-Lua Cristina Zotica, Sigurd Skogestad, Adchem Conference, Shenyang, China. July 2018 ,
Process

## Slide 36: MV-CV switching (because reach constraint on MV)
Simple CV-MV switching
  Don’t need to do anything if we followed the Input saturation rule:
  “Pair a MV that may saturate with a CV that can be given up (when the MV saturates)”

## Slide 37: Example: Avoid freezing in cabin
Simple MV-CV switching
    Keep CV=T>Tmin = 8C in cabin in winter by using MV=heating
    If it’s hot outside (>8C), then the heat will go to zero (MV=Q=0), but this does not matter as the constraint is over-satisfied.
Minimize u (heating), subject to

## Slide 38: Example: Anti-surge control (= min-constraint on F)
Simple MV-CV switching
We satisfy the input saturation rule:
«Pair a MV =z that may saturate with a CV =F that can be given up (when the MV saturates at z=0)”
    Keep minimum flow Fmin for pump or compressor using recycle valve.
    If the flow F0 (and thus F) becomes large then the recycle valve will close (MV=0), but this does not matter as the constraint on F is over-satisfied.
Minimize u (recycle), subject to

## Slide 39
p0
F0
F
p
QUIZ Compressor control
Suggest a solution which achieves
p< pmax= 37 bar (max delivery pressure)
P0 > pmin = 30 bar (min. suction pressure)
F < Fmax = 19 t/h (max. production rate)
F0 > Fmin = 10 t/h (min. through compressor
to avoid surge)
CW
p0
F0
F
p
CW
FC
PC
PC
FC
MAX
pmin=
30bar
Fmax=
19 t/h
pmax=
37bar
Fmin=
10 t/h
z
SOLUTION
All these 4 constraints are satisfied by a large z
-> MAX-selector
MAX
z
Zmin=0
MAX
z
Zmin=0
FC

## Slide 40: MV-CV switching (because reach constraint on MV)
Simple CV-MV switching
  Don’t need to do anything if we followed the Input saturation rule:
  “Pair a MV that may saturate with a CV that can be given up (when the MV saturates)”
Complex MV-CV switching
Didn’t follow input saturation rule
This is a repairing of loops
Need to combine MV-MV switching with CV-CV-switching
  The CV-CV switching always uses a selector
  As usual, there are three alternatives for the MV-MV switching:
    Split range control (block /\): Has problems because limits may change
    Several controllers with different setpoints (often the best for MV-CV switching)
    Valve position control (Gives «long loop» but avoids repairing).
Start 19/11-24

## Slide 41: Example: Furnace control
TC
u=Fuel gas
Flue gas
Process fluid
Air
T1s = 500C
TC
T2max=700C
LS
y1=T1
y2=T2
uA
uB
u=min(uA,uB)
Furnace control : Cannot give up control of y1=T1. What to do?
Inputs (MV)
u = Fuel gas flowrate
u2 = Process flowrate
Output (CV)
y1 = process temperature T1
(with desired setpoint)
u2
MIN
Complex MV-CV switching
Normally u2
is used for something else

## Slide 42: Cannot give up controlling T1 Solution: Cut back on process feed (u2) when T1 drops too low
TC
u=Fuel gas
Flue gas
Process fluid
Air
T1s = 500C
TC
T2max=700C
LS
y1=T1
y2=T2
uA
uB
u=min(uA,uB)
TC
T’1s = T1s-5C=495C
u2
TC
Using MV-MV switching
Inputs (MV)
u = Fuel gas flowrate
u2 = Process flowrate
Output (CV)
y1 = process temperature
(with desired setpoint)
Note: Standard Split Range Control (Alt. 1) is not good here for MV-MV swiitching.
Could be two reasons for too little fuel
  Fuel is cut back by override (safety)
  Fuel at max,
So don’t know limit for MV1 to use in SRC-block.
Complex MV-CV switching
u = input = manipulated variable (MV)
y = output = controlled variable (CV)
MIN
MIN
CV-CV switching
Desired:

## Slide 43: Use Alt. 2: Two controllers
TC
u=Fuel gas
Flue gas
Process fluid
Air
T1s = 500C
TC
T2max=700C
LS
y1=T1
y2=T2
uA
uB
u=min(uA,uB)
Inputs (MV)
u = Fuel gas flowrate
u2 = Process flowrate
Output (CV)
y1 = process temperature
(with desired setpoint)
TC
T’1s = T1s-5C=495C
u = input = manipulated variable (MV)
y = output = controlled variable (CV)
MIN
Complex CV-MV switching
u2
MIN

## Slide 44: Systematic design of simple advanced controllers (APC)
First design simple control system for nominal operation
  With single-loop PID control we need to make pairing between inputs (MVs) and outputs (CVs):
  Should try to follow two rules
    «Pair close rule» (for dynamics).
    «Input saturation rule»:
Process

## Slide 45
Disturbance
F1 [m3/s]
Example : Level control
LC
SP
FC
F10,m
F0,s
F0 [m3/s]
MV1 = z0 (inflow valve position)
MV2 = z1 (outflow valve position) (likely to saturate)
CV1 = F0 (inflow): Should be controlled at setpoint F0,s (if possible)
CV2 = level: must always be controlled (at some SP)
Problem: outflow-valve may saturate at fully open (z1=1) and then we lose level control
Note: We did not following the “input saturation rule” which says:
Pair MV that may saturate (z1) with CV that can be given up (F0)
z1
z0
Nominal design (follow “pair-close” rule)
Process
z1

## Slide 46
Disturbance
LC
Reverse pairing (follows “input saturation rule”):
FC
SP
F0,m
F0,s
BUT with Reverse pairing: Get “long loop” for F0
In addition: loose control of y2= level if z0 (F0-valve) saturates
F0 [m3/s]
F1 [m3/s]
«long loop»
This gives simple MV-CV switching (if z1 saturates at fully open)
«Long loop» = Works through other loops
z0

## Slide 47
Disturbance
LC
FC
SP-L
F0,m
F0,s
Alternative solution: Follow “Pair close”-rule and use Complex MV-CV switching.
When z1 saturates at max, use the other MV (z0) for level control and give up controlling F0
Get: “Bidirectional inventory control”
LC
SP-H
MIN
F0 [m3/s]
F1 [m3/s]
LC
Using
MV-MV
switching
This is complex MV-CV switching
Three alternsatives for MV-MV switching
SRC (problem since F0s varies)
Two controllers
VPC (“Long loop” for z1, backoff)
z1
CV-CV
switching
F’0,s

## Slide 48: Alt. 3 MV-MV switching: VPC
Disturbance
F1 [m3/s]
LC
SP
FC
F10,m
F0,s
F0 [m3/s]
z1
z0
z1,s = 0.9
(must be lower than 1=fully open, back-off)
MIN
VPC
VPC: “reduce inflow (F0) if outflow valve (z1) approaches fully open”
z1
Bidirectional inventory control
F’0,s

## Slide 49: Alt. 2 MV-MV switching: Two controllers (recommended)
Disturbance
LC
FC
SP-L
F1,m
F0,s
SP-L = low level setpoint
SP-H = high level setpoint
LC
SP-H
MIN
F0 [m3/s]
F1 [m3/s]
In addition: Use of two setpoints is good for using buffer dynamically!!
F’0,s
z1
Use low setpoint when level is controlled by product (outflow): Have room for feed if outflow stops temporarily.
Use high setpoint when level is controlled by feed (inflow): Can keep producing if inflow stops temporarily.
Bidirectional inventory control

## Slide 50: Inventory control for units in series and TPM
TPM (“gas pedal”) = Variable used for setting the throughput/production rate (for the entire process).
Where is the TPM located for the process?
  Usually at the feed, but not always! To maximize production: Locate close to bottleneck
  Important for dynamics
  Determines the inventory control structure
Rule (Price et al., 1994): Inventory control (Level and pressure) must be radiating around TPM:
TPM
TPM
TPM
TPM = Throughput manipulator

## Slide 51: Inventory control and TPM
Inventory control: Usually control of level and pressure
Throughput manipulator (TPM): Where the operator sets production rate
Usually TPM at feed, but better for economics: Close to production bottleneck
Radiation Rule for level and pressure control («to keep things flowing»): Inventory control should be radiating around TPM

## Slide 52: Rules for inventory control
Rule 1. Cannot control (set the flowrate) the same flow twice
Rule 2. Controlling inlet or outlet pressure indirectly sets the flow (indirectly makes it a TPM)
Rule 3. Follow the radiation rule whenever possible
Breaking the radiation rule leads to undesirable «long loops»*:
*A «Long loop» does not follow the «pair close» rule, and the functioning of a long loop depends on other loops being closed.
TPM
Comment: Originally the TPM was at the feed (F0) - but then the outflow (F3) reached saturation (so this became the TPM) – and we let F0 take over the inventory control in the last unit.
This may work OK if the inventory control in units 1 and 2 is very fast.
Unit 3
Unit 2
Unit 1

## Slide 53
QUIZ. Are these structures workable (consistent)? Yes or No?
TPM
TPM
TPM
TPM
Hint: What happens to the mass holdup inside the red box? Is it self-regulated?

## Slide 54
Quiz 2. Gas-liquid separator.
Where is TPM? Consistent (One is not)?
TPM
TPM
TPM
TPM:
control exit pessure
Case (a): Given feedrate. Could alternatively set p0
Cases (b) and (c): Gas production limiting
Case (d): Liquid production limiting
TPM
Doesn’t follow radiation rule +
Cannot have two TPMs
Rule: Setting in-pressure p0 sets inflow = TPM at inlet or inlet direction (no cases above)
Setting out-pressure pG sets outflow = TPM at outlet or outlket direction (offdiagonal two cases)
(a)
(d)
(b)
(c)

## Slide 55: Inventory control for units in series
Follows radiation rule
Does NOT follow radiation rule
Radiating rule:
Inventory control should be ‘‘radiating’’ around a given flow (TPM).
TPM
TPM
TPM
TPM

## Slide 56: Generalization of bidirectional inventory control
Reconfigures automatically (to follow «radiation rule!) with optimal buffer management!!
F.G. Shinskey, «Controlling multivariable processes», ISA, 1981, Ch.3
Cristina Zotica, Krister Forsman, Sigurd Skogestad ,»Bidirectional inventory control with optimal use of
intermediate storage», Computers and chemical engineering, 2022
,
Maximize
throughput:
Fs=∞
Bidirectional inventory control

## Slide 57
F0=1
F2=1
F3=1
F1=1
1
=∞
=∞
=∞
Given product flow
All levels are high (SP-H)

## Slide 58
F0=1
F2=1
F3=1
F1=0.5
1
=∞
=∞
0.5
Temporary reduction in flow F1 (feed to unit 2)

## Slide 59
F0=0.5
F2=1
F3=1
F1=0.5
1
0.5
=∞
=∞
Level 1 constant:
Reduction in feed to unit 1
Level in unit 2 drops

## Slide 60
F0=0.5
F2=0.5
F3=1
F1=0.5
1
0.5
=∞
=∞
Level 2 reaches SP-L:
Flow reduction
moves to unit 3

## Slide 61
F0=0.5
F2=0.5
F3=0.5
1
=∞
=∞
Flow reduction reaches product after some time
0.5

## Slide 62
F0=0.5
F2=0.5
F3=0.5
F1
1
=∞
=∞
=∞
Temporary flow reduction in F1 is over.
Get z1=1 (fully open).
System recovers: Temporary need F0 > 1

## Slide 63
F0=1.6
Fully open
F3=1
z2=1:Fully open
1
=∞
=∞
=∞

## Slide 64
F0=1
F2=1
F3=1
F1=1
1
=∞
=∞
=∞
Final steady state
All levels are high (SP-H)

## Slide 65
F0=1
F2=1
F3=1
F1=1
1
=∞
=∞
Challenge: Can MPC be made to do his? Optimally reconfigure loops and find optimal buffer?
YES. Use «trick»/insight of unachievable high setpoints on all flows

## Slide 66
Extension . Bidirectional inventory control with minimum flow for F2
Max flow: Fs=∞
𝐿 = 10%,
𝑀𝐿 = 40%,
𝑀𝐻 = 60%
𝐻 = 90%.
16 July 2022

## Slide 67: Don’t need bidirectional control on all units
IC
MIN
H
L
IC
MIN
H
L
IC
MIN
H
L
IC
MIN
H
L
MIN
IC
MIN
H
L
IC
MIN
IC
IC
H
L
MIN
small holdup
small holdup
«Long loop» can be OK in some cases

## Slide 68: Important insight
Many problems: Optimal steady-state solution always at constraints
In this case optimization layer may not be needed
  if we can identify the active constraints and control them using selectors

## Slide 69
Extension . Bidirectional inventory control with minimum flow for F2
Max flow: Fs=∞
𝐿 = 10%,
𝑀𝐿 = 40%,
𝑀𝐻 = 60%
𝐻 = 90%.
16 July 2022

## Slide 71: Inventory control (level, pressure)
All inventories (level, pressure) must be regulated by
  Controller, or
  “self-regulated” (e.g., overflow for level, open valve for pressure)
  Exception closed system: Must leave one inventory (level) uncontrolled
Usually only one TPM
  To get consistent mass balance: Can only fix same flow once
  But there are exceptions
    Multiple feeds (they are then usually set in ratio to the “main” TPM)
    Recycle systems often have a flow that can be set freely
Rule for maximizing production for cases where we cannot rearrange inventory loops: Locate TPM at expected bottleneck
  Otherwise you will need a “long loop” and you get loss in production because of backoff from constraint

## Slide 72
Suggest a control structure
What if we want to control p2 instead of p?
QUIZ
What happens if we
don’t follow the radiation rule?
Answer: Go to saturation, so one loop fails.

## Slide 73
FC
PC
The «obvious» pair-close pairing os OK. However, interactions between loops may be severe. Suggest tuning the FC first, and the PC about 5 times slower.

## Slide 74
FC
PC
(b)
F3 = c3(p2-pend)1/2
z1 to
fully open
(lose control
of F1)
Or: z2 to
fully open
(lose control
of p2)
Disturbances
in F1, p2, pend
Opposite
Disturbances
NO!
Not consistent

## Slide 75: Distillation example.
“Systematic Design of Active Constraint Switching Using Classical Advanced Control Structures”
Adriana Reyes-Lúa and Sigurd Skogestad
Industrial & Engineering Chemistry Research 2020 59 (19), 9342-9342
Can be given up
CV1=xB (cannot be given up)
MV1=V (can reach max)
MV2=L (normally used for xD)
MV3=F (has setpoint)
Spec. is max 5% heavy in top, but heavy in top gives economic loss. Economic optimal over-purification of top product (xDopt) depends on prices p
Bottom product is the most valuable and should always be kept at its purity constrant (xBmin).
Split range control*:
Normally we control xB with V
If V reaches Vmax then we instead use reflux L (and give up xDopt)
If L is not availabe (beacuse it’s used to control sDmin) then we instead use the feedrate F to control xB
*Split range control can be replaced by three controllers with different setpoints for xB
=95% light
=95% heavy
=98%
TC
This is an example where MPC may be preferred

## Slide 76: Alternative solution with different setpoints
Cannot be given up
=95% light
= 94% light
This solution looks simpler, but it is not as good dynamically in cases where we need to limit feed F to the column.
We then use F to control top composition, and L to control bottom compoistion.
The reverse pairing is better (which is what we get with the other solution)
=98% (but can change and be lower if energy (V) is expensive, so this is the reason for the max-selector)

## Slide 77
Simulation of alternative solution. The problematic pairing is used toward the end (t>80), but it’s not really tested because there are no disturbances

## Slide 78: Systematic design of simple advanced controllers (APC)
Then make a list of possible new contraints that may be encountered (because of disturbances, parameter changes, price changes)
Reach constraint on new CV
  Simplest: Find an unused input (simple CV-MV switching)
  Otherwise: CV-CV switching using selector (may involve giving up a CV-constraint or a self-optimizing CV)
Reach constraint on MV (which is used to control a CV)
  Simplest (If we followed input saturation rule):
    Can give ip controlling the CV (Simple CV-MV switching)
    Don’t ned to do anything
  Otherwise (if we cannot give up controlling CV)
    Simplest: Find an unused input
      MV-MV switching
    Otherwise: Pair with a MV that already controls another CV
      Complex CV-MV switching
      Must combine MV-MV and CV-CV switching
Is this always possible? No, pairing inputs and outputs may be impossible with many constraints.
May then use MPC instead

## Slide 79: Conclusion Advanced process control (APC)
Classical APC, aka «Advanced regulatory control» (ARC) or «Advanced PID»:
  Works very well in many cases
  Optimization by feedback (active constraint switching)
  Need to pair input and output.
    Advantage: The engineer can specify directly the solution
    Problem: Unique pairing may not be possible for complex cases
  Need model only for parts of the process (for tuning)
  Challenge: Need better teaching and design methods
MPC may be better (and simpler) for more complex multivariable cases
  But MPC may not work on all problems (Bidirectional inventorycontrol)
  Main challenge: Need dynamic model for whole process
  Other challenge: Tuning may be difficult