## Slide 1: Transfer function
Some typical transfer functions:
First-order with delay process, G(s)=k e-θs/(τs+ 1)
  Example: Heated tank with delay in heater, y=T, u=Q,
  V dT/dt = qin(Tin-T(t)) + Q(t- θ) /(ρcP) Get τ = V/qin and k=1/(ρcPV)
Integrating process, G(s)=k’/s
  Example: y = level (V) and u=qin, dV/dt = qin – qout Get k’=1
PID-controller , C(s) = Kc(1 + 1/(τIs) + τD s) («ideal PID»)
G(s)
u(s)
y(s) = G(s) u(s)
G(s) = transfer function of linear dynamic system
u and y: deviation variables
s: Laplace variable (replaces t as independt variable).
Note (may be confusing): s has units s-1 = second-1
Can just multiply G and u!

## Slide 2: First-order system
y(s) = G(s) u(s)
Two standard forms of first-order system:
1. G(s) = b/(s-a) where a = pole («state space» form)
Follow from general case with A=a, B=b, C=1, D=0.
  Note:
  k’=b=initial slope
  Time response to step M in u(t):
    Stable for a<0 since exp(at) =0 as t->∞
    Unstable for a>0 since exp(at) -> ∞ as t->∞
2. G(s) = k/(τs+1) (time constant form for stable system)
  τ = -1/a
  k=g(0) = -b/a = steady-state gain
  Time response to step M in u(t): y(t) = kM (1 - exp(-t/τ))

## Slide 3: General procedure, matrix state-space form
General* Nonlinear dynamic model:
  dx/dt = f(x,u,d), y = g(x,u,d) (x is vector of states, y is vector of “outputs”)
Steady state model. dx*/dt=0 -> f(x*,u*,d*)=0
  Find steady state *. Typically, use to find missing data
Introduce deviation variables and linearize
  dx/dt = Δf = A Δx(t) + B Δu(t) + Bd Δd(t). A =
  Δy(t)= Δg = C Δx(t) + D Δu(t) + Dd Δd(t)
Laplace** of both sides of linear model* (t -> s)
  sx(s) = A x(s) + B u(s) + Bd d(s)
  y(s) = C x(s) + D u(s) + Dd d(s)
Algebra (eliminate x(s), see next page)
  y(s) = G(s) u(s) + Gd d(s)
  Transfer matrix, G(s) = C (sI-A)-1B + D,
  Gd(s) = C (sI-A)-1Bd + Dd
Block diagram
Controller design
*State-space form (differential equations) is not completely general:
1) Cannot handle time delay.
2) Let g(s)= n(s)/d(s). Must assume: order d(s) ≥ order n(s) (so cannot handle ideal PID)
**We will only use Laplace for linear systems!

## Slide 4: General* Transfer Matrix
The n roots (generally complex) of the polynomial d(s),
d(s) = det(sI-A)=0
are the same as the eigenvalues of the state matrix A, and are known as the «poles» of the system.
A system with n states (so A is a nxn matrix) has n roots = eigenvalues = poles
*Warning: Not completely general. Does not include time delay, which cannot be written as a polynomial in s, and must assume order d(s) ≥ order n(s)..

## Slide 5: Plan for next two weeks
First-order systems (SiS5)
3. Second-order systems
  Can have oscillations (complex poles)
4. Closed-loop transfer function (with control)
5. Poles and zeros
  Including inverse response (RHP-zeros)
6. Slow oscillations for PI-control of integrating process
7. Approximating transfer functions
  Time delay
  Half rule
8. Derivation of SIMC PID rules (SiS6)

## Slide 6: Initial and final values for step response
Transfer function g(s)
  y(s) = g(s) u(s)
Deviation variables for y(t) and u(t)
Consider response y(t) to step of magnitude M in input.
  u(t) = 0 for t>0, u(t) = M for t≥0 u(s)=M/s
From g(s) we get directly final and intital part of time response:
Start here lecture 2 in week 5 (19/9-24)

## Slide 7
0
5
10
15
20
25
30
35
40
0
0.5
1
1.5
2
2.5
3
Step Response
Time (seconds)
Amplitude
s=tf('s')
g1 = 2/(10*s+1)
step(g1,50)
axis([0 40 -0.2 3])
Example g1 (k=2, ¿=10)
/)
y
u
y(t)
u(t)
63%
M
kM
Example: First-order system
Time response: y(t) = kM (1 - exp(-t/τ))
Initial slope (for M=1): k/τ = 2/10 = 0.2

## Slide 8
g2
g3
g1
s=tf('s')
g1 = 2/(10*s+1), step(g1,50)
axis([0 40 -0.2 3]); hold on,
g2 = 2/(12*s+1), step(g2,50)
g3 = 2.2/(10*s+1), step(g3,50)
g2: Change time constant τ from 10 (g1, blue) to 12 (g2, green) ….gives smaller initial slope & slower dynamics
g3: Larger steady-state gain (k=2.2) (red).
  Gives larger initial slope than g1 (but dynamics are not faster than g1, because also steady-state is larger)
First-order system responses
Time response: y(t) = kM (1 - exp(-t/τ))

## Slide 9: Integrating system, g(s)=k’/s. Special case of first-order system with ¿=∞ and k=∞ but slope k’=k/¿ is finite
0
5
10
15
20
25
30
35
40
0
0.5
1
1.5
2
2.5
3
Step Response
Time (seconds)
Amplitude
g2
g1
g4=0.2/s
g3
s=tf('s')
g1 = 2/(10*s+1), step(g1,50)
axis([0 40 -0.2 3]); hold on,
g2 = 2/(12*s+1), step(g2,50)
g3 = 2.2/(10*s+1), step(g3,50)
g4 = 2/(10*s+0), step(g4,50)
Example:
g4: Integrating system =0.2/s
g1 & g4: Same initial response (slope = 0.2=k/¿)
Large ¿: g(s)=k/(¿ s+1) k/(¿ s) = k’/s
Step response (u=M): y(t)/M = k’t (ramp)

## Slide 10
g6: Unstable system (e.g., exothermic reactor):
Note: Sign change in denominator d(s)
0
5
10
15
20
25
30
35
40
0
0.5
1
1.5
2
2.5
3
Step Response
Time (seconds)
Amplitude
g1 =
2
--------
10 s + 1
g4 =
2
----
10 s
g6 =
2
--------
10 s - 1
g4
g1
stable
g6
unstable
Integrating system:
on the limit to unstable
Oops… Negative sign in d(s)… Pole p=0.1 Unstable!

## Slide 11: 2nd order system. Special case: Two first-order in series
Example: Temperature in two tanks in series, τ1=V1/q, τ2 = V2/q
Conclusion: Step response (M = change in input):
(5-47)
(1) y(s) = G(s) u(s) with u(s)=M/s (step).
Partial fraction expansion of (1)
(2) y(s) = kM ( + where C0=1, C1=-τ1/(τ1- τ2), C2=τ2/(τ1- τ2)
(Find C0, C1 and C2 from (1)=(2)).
Inverse Laplace of (2)
y(t) =e+ e)

## Slide 12: Step response for two first-order in series: S-shaped response
Two second-order systems
with tau1+tau2=1:
g2a = 1/((0.5*s+1)*(0.5*s+1))
g2b = 1/((0.9*s+1)*(0.1*s+1))
Compare with first-order system with tau=1
g1 = 1/(s+1) (Black line)
g2b = 1/((0.9*s+1)*(0.1*s+1))
g1b = exp(-0.1*s)/(0.9*s+1)
Note: Second-order system with tau1 much larger than tau2 can be approximated as first-order plus delay with delay = tau2:
S-shaped: Initial slope=0 for g2a and g2b

## Slide 13
0
5
10
15
20
25
30
35
40
0
0.5
1
1.5
2
2.5
3
Step Response
Time (seconds)
Amplitude
g1 = 2/(2*s+1), step(g1,50)
g2 = 2/(2*s+1)^2, step(g2,50)
g3 = 2/(2*s+1)^3, step(g3,50)
g4 = 2/(2*s+1)^4, step(g4,50)
g5 = 2/(2*s+1)^5, step(g5,50)
g6 = 2/(2*s+1)^6, step(g6,50)
g7 = 2/(2*s+1)^7, step(g7,50)
g1
g7
n identical first-order systems in series
Note: More poles (relative to zeros) gives flatter initial step response. Proof:
For system with poles excess= m = np-nz, we get that g(s) ~ 1/sm when s goes to infinity.
Then the m’th derivative, y(m)(t), is finite (non-zero) for step-response. The other m-1 derivatives of y(t) are zero!
Example G1(s) = 2/(2s+1). m=np=1. So first derivative y’(t) (initial slope) is non-zero
Example G7(s) = 2/(2s+1)^7. m=np=7. So six first derivatives of y(t) are zero -> Very flat initial response. Almkost like time delay.
g2

## Slide 14
Roots (poles, eigenvalues):
Chapter 5
1. Two real poles (overdamped), ³ >1: Two first-order in series
General 2nd order system
(5-47)

## Slide 15: 2. Complex poles, |³|<1
y(s) = G(s) u(s) with u(s)=M/s (step).
Inverse Laplace
y(s) = kM ( + ) -> y(t)/kM =e+e
Complex poles give oscilllations!
Use Euler’s formula for complex parts:
The complex parts in y(t) cancel!
Finally get for y(t)/kM:
ω/σ = Complex-part/Real-part
ω = Complex-part

## Slide 16
Table 3.1 Laplace Transforms for Various Time-Domain
Functionsa (continued)
f(t) F(s)
Appendix A
Alternative forms of step
response for oscillating
2nd order system (0<zeta<1)

## Slide 17
Chapter 5

## Slide 18
s=tf('s')
zeta=0.5, tau=1
g = 1/[(tau*s)^2 + 2*tau*zeta*s + 1]
step(g,20)
g =
1
-----------
s^2 + s + 1
>> pole(g)
ans =
-0.5000 + 0.8660i
-0.5000 - 0.8660i

## Slide 19
s=tf('s')
zeta=0, tau=1
g = 1/[(tau*s)^2 + 2*tau*zeta*s + 1]
g =
1
-------
s^2 + 1
step(g,20)
pole(g)
ans =
0.0000 + 1.0000i
0.0000 - 1.0000i
PERSISTENT OSCILLATIONS
(Zero damping. On the limit to instability)

## Slide 20
Chapter 5
=a/b
=c/a
tp=π/ω
OS=exp(πσ/ω)
DR = OS2
P=2tp=2π/ω
|ζ|<1
a/b=
c/a=
d/b = undershoot
d

## Slide 22
Underdamped (Oscillating) second-order systems (|³|<1)
Corresponds to complex poles,
Process systems:
Oscillations are usually caused by (too) aggressive control
U-tube is an exception (see example next slide)
Example 1: P-control (controller gain Kc) of second-order process, g(s) = k/(¿1 s+1)(¿2 s+1)
  Oscillates (³<1) if Kck is large
But there also cases where we need «aggressive» control to avoid oscillations:
Example 3: PI-control of integrating process, g(s)=k’/s
  Need control to stabilize
  Oscillates (³<1) if Kck’ is small (!)
COMPLEX POLES IN PRACTISE

## Slide 23
Note: The system is linear
P≈1.40s

## Slide 24: Example 1. Setpoint response for P-control of 2nd order process
g(s) = k/[(4s+1)(s+1)]
P-controller: c(s) = Kc
Task: Derive closed-loop transfer function T(s) for setpoint change (can set d=0).
Note: same example as before
2024: Start week 6 (only 2 lectures this week)

## Slide 25
Offset = 1 – kKc/(1+kKc) = 1/(1+kKc)
= 1/5 = 0.2
Can also find ω from poles
0.8 s2 + s + 1 = 0
Solution:
s = -0.625 ± 0.927i
ys=1
Note: Larger value of Kc gives less offset but more oscillations.
Oscillations (complex poles) for Kc>0.5625.
g(s) = k/[(4s+1)(s+1)], gm=1
P-controller: c(s) = Kc . Data: Kck = 1
0.8

## Slide 26: Closed-loop transfer function
(1) Process: y = g(s) u + gd(s) d
(2) Controller: u = c(s) (ys-ym)
(3) Measurement: ym = gm(s) y + n
Closed-loop response: Want to find effect of ys , d an n on output y.
Task: Eliminate u and ymto find
y = T(s) ys + Td(s) d + Tn(s) n
gm
n (measurement noise)

## Slide 27: Closed-loop transfer functions
Closed-loop output response: y = T ys + Td d + Tn n
Introduce «loop»= L = g c gm
  T(s) = gc/(1+L)
  Td(s) = gd/(1+L)
  Tn = - T
General rule for negative feedback:
  Transfer function = «direct(s)» / (1 + «loop(s)»)
Example: What is response from ys, d and n to u?
  u = Tus ys + Tud d + Tun n
    Note that Tud = -T for input disturbance (gd=g) and gm=1
      which is interesting since with SIMC-rule we choose desired T, so we also «have control» over input change for disturbances
gm
n (measurement noise)

## Slide 28: Sensitivity function S
S gives effect of feedback
Tcl = Direct*S where S=1/(1+loop)
    No control: S=1 (S=I for multivariable case)
    Want |S| small to have small control error |e|:
      e = S (ys – gm gd d)
    Perfect control (infinite c): S=0 (Achievable at steady state with I-action)
gm
n
loop = g c gm

## Slide 29: Steady-state offset with P-control (k=process gain, Kc= controller gain)
e
Sensitivity fuction: S(s) = 1/(1+L) where L(s)=loop = g c gm.
S is transfer function from ys to control error e (since «Direct»=1): e = S(s) ys
Steady-state offset to step change in setpoint: e = S(0) ys where
S(0)= 1/(1+loop(0))= 1/(1+Kck )
since g(0)=k, c(0)=Kc, gm(0)=1
Example P-control. k=1, Kc = 4. Relative Steady-state offset e/ys is S(0)=1/(1+Kck ) = 1/5= 0.20 (20%)
Note with I-action (PI-control): Get c(0)=, loop(0)= so S(0)=0 and get no steady-state offet.
gm

## Slide 30: Example 2. PI-control of 1st order process
Example.
g(s) = gd(s) = 2/(3s+1)
SIMC PI-controller, τc=0.5 (so we are speeding up the response relative to τ=3):
c(s) = , Kc= 3, τI =2
-> c(s) =

## Slide 31: y= T(s) ys
Example 2. PI-control of 1st order process
Setpoint response. ys=1, d=0
2nd order system with a zero
(No oscillation! The overshoot is from the zero polynomial n(s)=2s+1)
Initial slope =
= 2
Note: Reach 63% approximately at t=τc=0.5
% Matlab
s=tf('s')
g = 2/(3*s+1)
c = 3*(1 + 1/(2*s))
T = g*c/(1+g*c)
step(T)

## Slide 32: Input Disturbance response (gd=g)
Td =
0.6667 s
-----------------
s^2 + 2.333 s + 1
Initial slope =
= 0.67
Steady-state = = 0
«Open-loop»:
Disturbance response without control
«Closed-loop»: With feedback control
% Matlab
s=tf('s')
g = 2/(3*s+1)
c = 3*(1 + 1/(2*s))
Td=g/(1+g*c)
step(g,Td)
g = gd =
2
-------
3 s + 1
IMPORTANT:
The initial disturbance response
(with or without feedback control)
is always the same

## Slide 33: Comment: Adding delay gives oscillations, θ = 0.5 s
>> delay = exp(-0.5*s)
delay =
exp(-0.5*s) * (1)
>> L =g*c*delay
L =
12 s + 6
exp(-0.5*s) * -----------
6 s^2 + 2 s
>> T2 = L/(1+L)
Internal delays (seconds): 0.5 0.5
>> step(T2)
Setpoint response. ys=1, d=0
Unstable with θ = 1 s
Complicated T(s) with delays…
Need to use simulations
Comment: The SIMC-controller for the process g(s) = 2e-0.5s/(3s+1) with τc=θ=0.5 has Kc=1.5 and τI=3.

## Slide 34: Example 3. PI-control of integrating process (level)
g
c)
y = Δh
u = -Δqout
d = Δqin
LC
h
hs
qin
qout
MV=qout
FLOWSHEET:
BLOCK DIAGRAM:
Mass balance with constant density (V=Ah):
dV/dt = qin – qout
Deviation variables + linearize (well, it’s already linear!)
A dΔh/dt = Δqin(t) – Δqout(t)
Laplace
Δh(s) = = (k’/s) (u+d)
k’ = 1/A
V [m3]
Task: Derive condition to avoid «slow» ocillations that may occur when Kc is too small
*Yes, this may seem a bit strange, but for PI-control of integrating process you may get oscillatons when Kc is too small!
In addition, you may of course get the more common «fast» oscillations if Kc is too large because of «overreaction» with time delay.

## Slide 35: General rule to avoid slow oscillations:
Integrating process with PI-control:
G
)
Proof:
Need large controller gain and/or large integral time (!)

## Slide 36: Closed-loop responses
Td=
Note: This is not a good tuning,
Will get slow oscillations since
k’KcτI = 1*0.25*1=0.25 < 4

## Slide 37: Simulink, tunepid4

## Slide 38
0
5
10
15
20
25
30
35
40
0
0.5
1
1.5
2
2.5
%tunepid4
s=tf('s')
theta=0
g=(1/s)*exp(-theta*s) % integrating
taud=0
taui=1
Kc=0.5 % oscillations (Kc*k'*taui = 0.5 < 4)
sim tunepid4; plot(Tid,y); hold on %
Kc=0.25 % more oscillations (Kc*k'*taui = 0.25 < 4)
sim tunepid4; plot(Tid,y,'red');
Kc=1 % less oscillations (Kc*k'*taui = 1)
sim tunepid4; plot(Tid,y,'green');
hold off
Kc=0.5
Kc=1
Kc=0.25
PI-control of integrator (level control). G = 1/s, taui=1. VARY Kc
Input disturbance at t=20
Setpoint change at t=0
Note: Need higher controller gain
to reduce “slow” oscillations!
So would need to increase Kc to 4 in this case
(SIMC-rule)

## Slide 39
0
5
10
15
20
25
30
35
40
0
0.2
0.4
0.6
0.8
1
1.2
1.4
1.6
1.8
taui=0.5
taui=4 (SIMC)
taui=2
PI-control of integrator (level control). G = 1/s, Kc=1. VARY taui
Input disturbance at t=20
Setpoint change at t=0
So need to use taui=4 to have
no oscillations (SIMC-rule).
Get T(s)=(4s+1)/(2s+1)^2
Note: Need larger integral
time reduce “slow” oscillations

## Slide 40: Poles and zeros
g(s) = n(s)/d(s).
Example.
Standard forms:
1. Time constant form
2. Pole-zero form,
p=pole, z=zero
(more general, for unstable and
complex poles/zeros)

## Slide 41: Poles and zeros
Transfer functions G(s) of linear, time-invariant systems with time delay are ratios of two polynomials in s (Laplace variable)
  G(s) = n(s)/d(s)
Polynomials have roots. root in denominator, d(s)=0: G(s)   ”pole” (x) root in numerator, n(s)=0: G(s)  0 ”zero” (0)
Effect on dynamics:
  Poles determine stability and fast or slow dynamics
    d(s)=(τs+1). «Stable» LHP-poles slow down the response
      slower for large τ
    Poles in right half plane (RHP): Unstable .
      Example: g(s)=1/(s-1). Has RHP-pole at s=1
    Complex poles (=eigenvalues of A): Oscillations with frequency ω
      Example: g(s) = 1/(s^2 + s + 1). Solve d(s)= s^2 + s + 1 = 0. Get poles s1 = -0.5 + 0.87*i, s2 = -0.5 – 0.87*i, ω=0.87
  Zeros are responsible for shape of response
    n(s)=(Ts+1). Zeros in left half plane (LHP): «Lift» the response
      give overshoot for large T.
    n(s)=(-Ts+1). Zeros in right half plane (RHP): always give inverse response
      Inverse response makes problems for feedback control
      Example: g(s)=(-0.5s+1) / (10s^2+11s+1). Has RHP-zero at s=2
Re(s)
Im(s)
1
Re(s)
Im(s)
2
0
-0.5 + 0.87i
-0.5 - 0.87i

## Slide 42: Zeros
Zeros are common in practise
Occur when there are several «paths» to the output.
RHP zero: «competing effects where slow wins (has largest gain)»
Example 1.
Example 2
Example 3
g1(s)
g2(s)
u
y
All coefficients positive: LHP zero
Sign change: RHP zero ) Inverse response
0
5
10
15
20
25
30
35
40
0
0.5
1
1.5
2
2.5
Step Response
Time (seconds)
Amplitude
3
1
2
Note; Overshoot since 11.3>10
(overshoot: competing effects where fast wins)
Zeros
Example 2: RHP-zero with «time constant» -0.59: Similar to delay of 0.59.
10

## Slide 43
Zeros
Start here week 7

## Slide 44: Summary poles and zeros
G(s) = n(s) / d(s)=k’(s-z1) / (s-p1)(s-p2)..
Example: G(s) = 4 (3s-1)/(s2+s-2),
  Get: k’=12, z1=1/3, p1=-2 p2=1
Poles p (=eigenvalues of A-matrix)
  Determine speed of response, exp(p*t)
  Negative sign in d(s) ) p2 in RHP: unstable, exp(p2*t) ! 1 (NEED control)
  Pole p complex: oscillating response
Zeros z
  Determine shape of response
  Negative sign in n(s) ) z1 in RHP: inverse response (BAD for control)
  LHP-zero may give overshoot

## Slide 45: Approximation of time delay
Time delay is a bit difficult because it’s «infinite order»
  So cannot directly use with g(s)=n(s)/d(s) (where n and d are polynomials)
  or with «state-space» form (dx/dt=Ax+Bu)
Taylor expansion of ex (x=-θs)
Approximation of delay as n(s)/d(s):
Pade approximation (better)
n’th order Pade approximation (even better)
RHP-zero approximation (we use this for SIMC)
1st order approximation

## Slide 46: Simple approximations of time delay Example: Step response of first-order system plus delay
0
0.5
1
1.5
2
2.5
3
3.5
4
4.5
5
-1
-0.8
-0.6
-0.4
-0.2
0
0.2
0.4
0.6
0.8
1
Step Response
Time (seconds)
Amplitude
s=tf('s')
theta=1
g0=exp(-theta*s) % 0. Original time delay.
g1= - theta*s + 1 % 1. As RHP-zero.
g2= 1/(theta*s+1) % 2. As First order
g3 = (-theta*s/2+1)/(theta*s/2+1) % 3. Combined: Pade-approx
h=1/(s+1)
step(g0*h,g1*h,g2*h,g3*h)
axis([0 5 -1 1.1])
0
3
1
2
“Going the other way”

## Slide 47: n’th order Pade approximation
Accurate for large n
s=tf('s')
theta=1
g0 =exp(-theta*s) % Original time delay
g1 = (-theta*s/2+1)/(theta*s/2+1) % 1st-order Pade-approximation
g2 = (-theta*s/4+1)^2/(theta*s/4+1)^2 % 2nd-order Pade-approximation
g3 = (-theta*s/6+1)^3/(theta*s/6+1)^3 % 3rd-order Pade-approximation
h=1/(s+1)
step(g0*h,g1*h,g2*h,g3*h)
axis([0 5 -0.2 1.1])
Original delay
1
2
3
Why use Pade?
To get model on state space form, dx/dt=Ax+Bu
Note: Number of RHP-zeros
= number of 0-crossings of step response

## Slide 48: Approximations of transfer functions
Going the «other way»
Want to approximate g(s)=n(s)/d(s) as first-order plus delay
  «Skogestad half rule» to find effective delay. IMPORTANT!
  see slides SiS6 for SIMC-rule

## Slide 49: Extra: Examples of dynamic model structures
TexPoint fonts used in EMF.
Read the TexPoint manual before you delete this box.: AAAAAAAAA
How do we get zeros?

## Slide 50: RHP-zero (inverse response)
Q [W]
=const.
u=wH [kg/s]
T0=10C
wC [kg/s] = const.
T0=10C = const.
y = T [C]
Electric heater
Th
Mix
70C
40C
Response in y=T to a 10% step increase in u=wH =0.1:
38.5C
41.5C
40C
Two effects: 1) Direct effect of mixing: g1(s)=15
2) Indirect effect of changed Th: g2(s) = -30/(20s+1)
20s
}

## Slide 51: Model derivation
d3=Q [W]
u=wH [kg/s]
d2=T0
d1=wC [kg/s]
d2=T0
y = T [C]
Electric heater
x = Th
Mix

## Slide 52: Zero at 0 (no steady-state effect)
Q [W]
=const.
w[kg/s]=1=const.
T0=10C
y = T [C]
Electric heater
Th
Mix
70C
64C
Response in y=T to a step decrease in bypass fraction from 0.1 to 0.05:
64C
67C
Two effects: 1) Direct effect of mixing: g1(s)=-60
2) Indirect effect of changed Th: g2(s) = 60/(22s+1)
22s
}
Bypass (10%)
u = ® w [kg/s]
10C
Th
T

## Slide 53: Model derivation
Q [W]
w[kg/s]=1=const.
T0=10C=const.
y = T [C]
Electric heater
Th
Mix
70C
64C
Bypass, u = ® w [kg/s]
10C