## Slide 1: PID control. Practical issues
Smith Predictor (NOT PID…)
PID Controller forms
Ziegler-Nichols tuning
Windup
Digital implementation
TexPoint fonts used in EMF.
Read the TexPoint manual before you delete this box.: AAAAAAAAAA
Write on board

## Slide 2: Smith Predictor
SP looks good in theory. BUT: It’s sensitive to time delay error AND we have found that well-tuned PID (with τD = θ/3) is more robust and almost always better than Smith predictor controller* FORGET SP!
* Chriss Grimholt and Sigurd Skogestad. ''Should we forget the Smith Predictor?'' (2018) In 3rd IFAC conference on Advances in PID control, Ghent, Belgium, 9-11 May 2018. In IFAC papers Online (2018)

## Slide 3: PID controller
e(t) = ys – ym(t)
P-part: MV (Δu) proportional to error
    This is usually the main part of the controller! (except for static process with no dynamics except delay)
    Make sure Kc has the right sign! With negative feedback in the loop, Kc has the same sign as the process gain k.
    Problem: Gives steady-state offset if used without I-action. Offset= 100%/(1+Kck)
I-part: To avoid offset, add contribution proportional to integrated error.
    Note: Larger integral time τI gives less I-action (turn off by selecting tauI=9999)
    Sometimes called “reset time”
      Physical interpretation: τI is essentially the time it takes to “reset” the bias (u0).
    Note: Integral term keeps changing as long as e≠0
    -> Will eventually make e=0 (no steady-state offset!)
Possible D-part: Add contribution proportional to change in (derivative of) error
    Note: Larger derivative times more D-action (turn off by selecting taud=0).
    Can improve control for high-order (S-shaped) response, but sensitive to measurement noise
“Ideal/Standard” form:

## Slide 4: Sign of the controller gain
The most common error when tuning a controller is to use the wrong sign of the controller gain.
  One may think that this is easily detected, but I have seen loops that have been oscillating for years because of the wrong sign (which results in positive rather than negative feedback control).
The rule in a standard negative feedback implementation (with ys-y as the controller input) is that the sign of the controller gain (Kc) and the process gain (k) should be the same. For example, recall the SIMC-rule: Kc=(1/k)*(τ/(τc+θ)).
But: Most commercial control systems only allow for positive controller gains and then instead distinguish between «direct» and «reverse» control action.
  ”Reverse acting” is used in the normal case when the process gain (k) is positive
    because MV (u) should go down when CV (y) goes up (to get negative feedback), for example, when we use heat (u=Q) to control room temperature (y=T).
  ”Direct acting” is used when the process gain k is negative
    Comment: This convention is common in process control, including most vendors such as Emerson, Honeywell, ABB, Yokogawa and also the Aspen/Hysys simulation software. Here is from the Aspen/Hysys manual:
    BUT WARNING: Be careful and read the manual! Some people (maybe electrical engineers) use «direct» and «reverse» opposite!, e.g., wikipedia on PID control (2023): https://en.wikipedia.org/wiki/PID_controller
Note common process control notation:
y = PV (process value)
ys = SP
u = OP (output from controller)

## Slide 5
+ many more (see manual for your control system…)

## Slide 6: Series to ideal form
Derivation: See exercise 6. Problem 3
Note: The reverse transformation (from ideal to series) is not always possible because
the ideal controller may have complex zeros.

## Slide 7
ys
y
2. To avoid “derivative kick” :
Do not take derivative of setpoint ys
u
For smoother control/ less sensitivity to noise: Filter the measurement.
Must require
Typical 1/10 of closed-loop time constant :
1
®
¿
D
s
+
1
Practical “Ideal” PID
3. Also need to avoid “windup” of the integral action if u saturates (at umin or umax) so that at steady state. See next slide

## Slide 8: Integral windup
Problem: Input saturates so e(t) does not go to zero.
Integrator “winds up” u(t) when actual input has saturated
Actual input is m=.
m=u if no saturation
d

## Slide 9: Anti-windup
Many approaches to avoid windup
  Simplest: Limit u (=output from the controller) to be within specified bounds (by updating u0)
    For example, with Sigurd’s discrete controller (later)
  Better: Make integrator track true input using feedback correction (see Example, Exercise and Lab)
  Use discrete controller in velocity form
    BUT requires I-action
  Stop integration (e.g. set ¿I=9999) when saturation in input occurs (requires logic)
Approaches 1 or 2 are recommended

## Slide 10: Anti-windup with tracking (approach 2)
The idea is to «back-calculate» a correction so that u’ tracks u. That is, we want to avoid «wind-up» of the error
eT = – u
where
u = desired input = output from the controller
= m = actual input.
could be different from u for many reasons:
Saturation (u is valve position, as shown in Fig. 3)
Selector (so another controller determines u)
Cascade control (e.g., caused by saturation in the inner loop)
  In this case u=y2s and =y2
Choice of tracking time: A common choice is τT=τI (= integral time) or equivalently
Note: for with τT=τ, a simple positive feedback implementation of the I-action («external reset») can be used (see Exercise 11). This implementation is very common in commercial systems (ABB, etc.).
However, the above implementation is recommended because it gives an extra tuning pararmeter. Note that the best the tracking time may differ for each of the three cases (saturation, selector, cascade control)
How does it work? At steady-state the input to the intergrator is zero, and we have
  (Kc/tauI) e + (1/tauT) eT = 0
  -> eT= -u = (tauT/tauI)*(Kc*e) (at steady state)
  Here Kc*e is the contribution from the P-action, so with the choice tauT=tauiI, the P-action will activate u (go out of saturation) if e «jumps» to 0, so just as y crosses its setpoint ysp. This may be a resasonable choice.
Choosing tauT smaller will activatate u earlier, which may be an advantage, for example, if we want to avoid that y overshoots its setpoint. On the other hand, this may make the «anti-windup» a bit nervous. For example, it may make the input u switch uncessesary out of saturation.
Example electric heater. In the summer, the heater is off (umin) and y=T > ys=Ts=22C. If it gets cold, then with a small value of tauT (less than tauI), the P-action will turn on the heater before y=T reaches its setpoint (22C), which may be good if we don’t like it cold. However, it may be a danger that the heat is turned on unnecessary (although it will only be for a short time as the integral action will turn it off again).
Simpler common «external reset» implementation where τT =τI . See Exercise 11 (Problem 3)

## Slide 11
g= 2/(10*s+1)
PI: Kc=1.25, taui=4
Input saturation: umax=0.1, umin=-0.1
Disturbance (d): Pulse from 0 to 0.2 and back to 0 at t=10
Example anti-windup (Approach 2)
Approach 2:
Feedback correction which makes u’ track u.
Gain2= KT = taui/tauT = tracking constant
Often KT= 1 is recommended (corresponds to have tracking time = integral time)
If KT is too high the P-action may make the system go out of saturation prematurely
No anti-windup: Set KT = 0.
d
File: tunepidantiwindup.mdl
u

## Slide 12
Black = with anti-windup (KT=1)
Blue = with anti-windup (KT=100)
3. Red = without anti-windup (KT=0)
u (with anti-windup)
Umin= -0.1
t=10: Disturbance starts
t=20: Disturbance ends
u (without anti-windup)
Note: The dashed lines are the input u
computed by the controller,
the real input does not go below -0.1 0
y(t)
setpoint
Black: With anti-windup (KT=1)
Much better! y(t) has only small undershoot
KT=100: Similar response (but recommend KT=1)
Red: Without anti-windup (KT=0):
Input u remains saturated to t=32
(long after disturbance is gone at t=20).
y(t) must overshoot on other side
for integral of y(t) to become zero.
u(t)

## Slide 13: Anti-windup with cascade control
Inner loop
Outer loop
valve
Selector: y2s tracks y2 when valve saturates*
u tracks
|.|
* The selector makes sure we use anti windup in the outer loop only when the inner loop (u) is saturating, and not just because the inner loop is a little slow.

## Slide 14: Bumpless transfer
We want a “soft” transition when the controller is switched between “manual” and “auto”
  or back from auto to manual
  or when controller is retuned
Simple solution: reset bias u0 as you switch, so that u(t) = umanual(t).

## Slide 15: Example: Control of floor heating
Exam Process control. Dec. 2024
Dynamic model:
G(s) (from Q to T)
2 min. of measurement noise
Matlab: and-limited white noise with noise power = 3 e-5, and sample yime 0 0.002h = 7.2s
15h
Gd(s)
PI
PI
P
P
y=T
u=Q
Want to control temperature y=T using floor heating u=Q.
Time in hours.
Model (Exam 2024): G = 30/(41s+1)(0.1s+1) = 30 / (4.1s^2 + 41.1s + 1) + delay 0.002h = 7.2s (delay not important)
Input (u=Q) is between 0 and 10.
Intital state (t=0): Q=0, T=To=0C.
t=0 Turn on controller with SP=15C.
t=5h Setpoint change to SP=20C
t=10h : To (disturbance) changes from 0C to -10C
SIMC, Kc = 1/k tau/(tauc+theta). tauI=min(tau, 4(tauc+theta).
From process model G: Have k=30, tau = 41, theta =0.052 (half rule),
PI-control. Choose tauc+theta=0.5h, (about 10 theta), Get Kc = (1/30)*41/0.5 = 2.7, taui = min (41, 4*4*0.5) = 2 h, KI = Kc/taui = 1.35
Anti-windup: Tracking coffeicient Kt=1 (same as "external reset", corresponds to tauT=tauI)
P-control: Can increase with same robustness since no I-action, so use Kc=3.
For P and PI control add filter with tauF=0.1*tauc=0.1*0.5=0.05h
P and PI without meas. filter
P and PI –control (both with measurement filter, tauF=tauc/10)
PI has anti-windup (Kt=1, «external reset»)
ON/OFF control
PI without anti-windup
Conclusion: P and ON/OFF are best
Note: No input disturbance on u=Q in this case (unusual) so I-action not needed
Ooops…
PI gives overshoot
Note: The residence time for air is 200 kg/0.04 kg/s = 5000 s = 1.39 h, and when we take into account the heat transfer to the floor, the time constant is only mcp/(UA+wcp) = 200/ (0.5+0.04) = 370s = 0.1 h. The time constant for the floor alone is only 5000 kJ/K/0.5 kW/K = 10000s = 2.7h. The very large time constant of 41h is caused by the interaction between the floor and the air.

## Slide 17: Optimal PID settings
Can find optimal settings using optimization
SIMC-rules are close to IAE-optimal for combined setpoints and disturbances (with given robustness in terms of Ms)*
*Chriss Grimholt and Sigurd Skogestad, ''Optimal PI and PID control of first-order plus delay processes and evaluation of the original and improved SIMC rules'' ,
Published in: J. Process Control, vol. 70 (2018), 36-46.

## Slide 18: Methods for online tuning of PID controllers
Trial and error
Ziegler Nichols (see Exercise 8, Problem 1)
  Oscillating P-control
  Relay method to get oscillations
Closed-loop response with P-control
  Shams method (see Exercise 8, Problem 1)
On-line tuning: Avoids an open-loop experiment, like a step input change.
Advantage on-line: Process is always “under control”
In practice: Both “open-loop” and “closed-loop” (online) methods are used

## Slide 19: Tuning of your PID controller I. “Trial & error” approach (online)
P-part: Increase controller gain (Kc) until the process starts oscillating or the input saturates
Decrease the gain (~ factor 2)
I-part: Reduce the integral time (I) until the process starts oscillating
Increase a bit (~ factor 2)
Possible D-part: Increase D and see if there is any improvement
Very common approach,
BUT: Time consuming and does not give good tunings: NOT recommended

## Slide 20: II. Ziegler-Nichols closed-loop method (1942)
P-control only: Increase controller gain (Kc) until the process cycles with constant amplitude:
Write down the corresponding “ultimate” period (Pu) and controller gain (Ku).
Based on this “process information” obtain PID settings:
(ideal)
PID is for ideal form
TL-modification is smoother
(smaller Kc and larger ¿I).
Main problems ZN:
  Too aggressive (and has no tuning parameter)
  Two pieces of information (Pu, Ku) is too little to capture all processes. Because of this
  ZN works poorly on static (delay-dominant) processes (the same applies to TL-modification)

## Slide 21
IMC has I=
Ziegler-Nichols is usually
aggressive
Setpoint change at t=0c
Input disturbance at t=20
Example PI. Integrating process with delay=1,
Process model: .
SIMC-tunings with (“tight tuning”):
Ziegler-Nichols:
Experiment: 1.57 (=π/2)
PI-control:

## Slide 22
Approximate as first-order model with k=1, 1 = 1+0.1=1.1, =0.1+0.04+0.008 = 0.148
Get SIMC PI-tunings (c=): Kc = 1 * 1.1/(2* 0.148) = 3.71, I=min(1.1,8* 0.148) = 1.1
2. Approximate as second-order model with k=1, 1 = 1, 2=0.2+0.02=0.22, =0.02+0.008 = 0.028
Get SIMC PID-tunings (c=): Kc = 1 * 1/(2* 0.028) = 17.9, I=min(1,8* 0.028) = 0.224, D=0.22
ZN-PI: Close to unstable
ZN-PID: unstable

## Slide 23: Åstrøm relay method (1984): Alternative approach to obtain cycling (and Ku)
Avoids operating at limit to instability
Use ON/OFF controller (=relay) were input u(t) varies +-d (around nominal)
Switch when output y(t) reaches +- a0 (deadband) (around setpoint; can use a0=0)
Example: Thermostat in your home
From this obtain Pu and
d: amplitude u(t) (set by user)
a: amplitude y(t) (from experiment)
Start lecture 2, week 8

## Slide 24: III. Shams’ method: Closed-loop setpoint response with P-controller with about 20-40% overshoot
Kc0=1.5
Δys=1
Δyu=0.54
Δyp=0.79
tp=4.4
Start from steady state and do step P-response
OBTAIN DATA IN RED (first overshoot
and undershoot), and then:
dyinf = 0.45*(dyp + dyu) % estimate dyinf (so don’t wait)
Mo =(dyp -dyinf)/dyinf % Mo=overshoot (about 0.3)
b=dyinf/dys % offset parameter
A = 1.152*Mo^2 - 1.607*Mo + 1.0
r = 2*A*abs(b/(1-b))
2. OBTAIN FIRST-ORDER with DELAY MODEL:
k = (1/Kc0) * abs(b/(1-b))
theta = tp*[0.309 + 0.209*exp(-0.61*r)]
tau = theta*r
3. CAN THEN USE SIMC PI-rule
Example 2: Get k=0.99, theta =1.67, tau=3.0
Ref: Shamssuzzoha and Skogestad (JPC, 2010) + modification by C. Grimholt (PID-book 2012)
See Exercise 8!
Δy∞
Alternative to Ziegler-Nichols closed-loop experiment: Obtains more information and avoids cycling.

## Slide 27: Effect of sampling
All real controllers are digital, based on sampling
¢t = sampling time (typical 1 sec. in process control, but could be MUCH faster)
Max sampling time (Shannon): ¢t < ¿c/2, but preferably much smaller (¿c = closed-loop response time)
With continuous methods: Approximate sampling time as effective delay µ = ¢t /2
Strange things can happen if ¢t is too large:
¢t =0.02
¢t
yk
Yk-1
Yk+1
k=present time

## Slide 28: Digital (discrete) implementation of first-order filter of measurement*
ym
y
*Equivalent to “exponentially moving average” of time series data. See Exercise 8, Problem 2
Tuning: Select ¿F = 0.1 ¿c
t
k
t-Δt
k-1
But: τF should be selected independent of Δt
Typical: τF = 0.1 τc (normally much larger than Δt).
Comment. «Normal» moving average (not as good) for last 10 measurements is

## Slide 29: Discrete (digital) implementation (practical in computer) of PID controller
This is Sigurd’s recommendation
= “Alt. 3” (see next page)
(Backward Euler)
e(t) = ys – y, y = filtered measurement
“How to program a PID controller in 5 minutes.” (In addition you should filter the measurement; see previous slide)
t
k
t-Δt
k-1
Normally: Use -dy/dt rather than de/dt
to avoid differentiation of setpoint

## Slide 30: Comparison with book: Digital implementation of PID controllers
Finite difference approximation:
?
ek = present sampled value = e(t)
ek-1 = previous sample = e(t-Δt)
ek-2 = e(t-2Δt)
Velocity form
=Bumpless
transfer
Note: p = output from controller
Alt. 1
Alt. 2
Alt. 3 (Sigurd’s with bias as extra state, better than Alt. 1 and Alt. 2)
? This is a major
disadvantage
of Alt. 2
Alt. 1 (position form)
Alt. 2 (velocity form)
only exceeds limits by small amount

## Slide 31: Conclusion: Digital implementation of ideal PID
This is from:
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Published in: Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages)
Ideal PID:

## Slide 33: Block diagram symbols

## Slide 34: Should I buy a valve positioner?
Usually not, if the valve is for automatic control
    But it may be difficult to avoid because most vendors include them
If you can measure the flow, then a slave flow controller eliminates the need to buy a valve positioner.
Also, the valve positioner is often slow (and tunings cannot be changed) and it then adds an effective delay which may make feedback control difficult

## Slide 35: Conclusion PID
Use SIMC-tunings for Kc, taui, taud
  Tuning parameter tauc
  Note that taud is for cascade PID form
Add filter on noisy measurements
  To avoid «nervous» MV (= controller output)
  First-order filter 1/(tauf*s+1).
    Typical tauf=0.1*tauc
    Overall controller (cascade form) is then: C(s) = Kc
    Usually taud=0 and often tauf=0.
Add anti-windup
  Recommend «input tracking».
    Tracking constant KT. Typical KT=1
May in some cases add filter on setpoint (2-DOF control)
  Less general approach: Use a different P-gain Kcs for the setpoint