## Slide 1: «Advanced» control
This is a relative term
Usually used for anything than comes in addition to (or in top of) basic PID loops
Main options
  Standard «Advanced regulatory control» (ARC) elements
    Cascade, feedforward, selectors, etc.
    This option is preferred if it gives acceptable performance and it’s not too complicated
  Model predictive control (MPC)
    Requires a lot more effort to implement

## Slide 2: Two fundamental ways of decomposing the controller
Vertical (hierarchical; cascade)
Based on time scale separation
Decision: Selection of CVs that connect layers
Horizontal (decentralized)
Usually based on distance
Decision: Pairing of MVs and CVs within layers
CV1
CV2
In addition: Decomposition of controller into smaller elements (blocks):
Feedforward element, nonlinear element, estimators (soft sensors), switching elements

## Slide 3: The decision hierarchy is based on “time scale separation”
Control layers:
Supervisory control (“Advanced classical control” or MPC):
  Follow set points for CV1 from economic optimization layer
  Switch between active constraints (change CV1)
  Look after regulatory layer (avoid that MVs saturate, etc.)
Regulatory control (PID):
  Stable operation (CV2)
CV = controlled variable
PROCESS
(day)

## Slide 4: Standard Advanced control elements
Each element links a subset of inputs with a subset of outputs
Results in simple local tuning
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages).

## Slide 5: If PID feedback control is not working well
First try retuning (SIMC-PID) or changing the pairing (E0)
  Of course, you need anti-windup (E8) if the input (MV) may saturate (dynamically)
Next: Advanced control:
The first thing to consider is cascade control (E1)
  Measure an output closer to the disturbance
  Often flow control slave
The next thing is feedforward control (E11)
  Ratio control (E2) is a must for mixing!
  Nonlinear feedforward based on steady-state model, y = f0(u,d): Use transformed input v=f0(u,d). (E14)
Next consider adding extra «fast» input
  Possibly with valve position control (E3) for original input
What about Constraints?
  Switching between constraints: Three cases: MV-MV (E5,E6,E7), CV-CV (E4), MV-CV
Multivariable control. If interactions are important
  Start with Single-loop control (Pairing)
  May try: Decoupling (E12, E14)
  May consider MPC if very interactive

## Slide 6: Standard “Advanced regulatory control” (ARC) elements Use when single-loop feedback control (PID) alone is not good enough
Design based on simple elements:
0. PID control with anti-windup
1. Cascade control (measure and control internal variable, y2)
2. Feedforward control (measure disturbance, d)
    Including ratio control
3. Extra MV dynamically: Alt. 1. Valve position control*(«Input resetting =midranging»)
  Alt. 2. Parallell control, e.g. one PI and one P.
4. MV saturates but have unused MV (MV-MV switching): Three options:
  Alt.1. Split range control
  Alt.2. Several controllers with different setpoints
  Alt.3. Valve position control *
5. Change in CV because reach new CV-constraint (CV-CV switching): Only one option: Selectors (max,min)
6. MV saturates: MV-CV switching
  “Do nothing” (use PID with anti windup) if we can give up controlling CV (follow “input saturation rule”)
  Otherwise: Combine MV-MV (three options) and CV-CV switching (selector)
7. Multivariable control (MIMO)
  Single-loop control (decentralized)
    “Pair close”(but avoid pairing on negative steady-state RGA elements), fast and slow loops for achieving decoupling
  Decoupling
    For interactive process (with strong couplings, e.g. where RGA is unfavorable).
    Two-way decoupling for 2x2 process. Think FF. Use reverse implementation with two blocks
    One-way decoupling can be used for larger systems
  MPC (model predictive control) is recommended for more complicated cases (can also replace most of the other elements above; in particular feedforward)
8. Calculation blocks, Input transformations (ratio, sums, etc.). For nonlinear decoupling, nonlinear feedforward, linearization
Trivial idea: y = f(u,d,) select transformed input v = f(u,d) sand solve for u. Too obvious or too complicated?
* VPC may be used in two different ways. Valve position control (VPC) is active all the time for case 3, but not for case 4 (MV-MV switching)
Constraint
Handling, see
Part 2 of APC slides

## Slide 7: MV-CV Pairing. Two main pairing rules (supervisory layer*):
“Pair-close rule” : The MV should have a large, fast, and direct effect on the CV.
“Input saturation rule”: Pair a MV that may saturate with a CV that can be .given up (when the MV saturates).*
  Exception: Have extra MV so we use MV-MV switching (e.g., split range control)
“ RGA-rule”
  Avoid pairing on negative steady-state RGA-element. Otherwise, the loop gain may change sign (for example, if the input saturates) and we get instability with integral action in the controller.
Most basic element: Single-loop PID control (E0)
Additional rule for interactive systems:
*For regulatory (stabilizing) control, we usually want to avoid using any MV that may saturate (so Rule 2 becomes: Avoid using a MV that may saturate), but for the supervisory layer this is not possible

## Slide 8: E1. Cascade control
Idea: make use of extra “local” output measurement (y2)
Implementation: Controller (“master”) gives setpoint to another controller (“slave”)
  Without cascade: “Master” controller directly adjusts u (input, MV) to control y (primary output, sometimes called y1)
  With cascade: Local “slave” controller(fast) uses u to control “extra”/fast measurement (y2). *
  “Master” controller (at least five times slower than slave) adjusts setpoint y2s.
Example: Flow controller on valve (very common!)
  y = level H in tank (or could be temperature etc.)
  u = valve position (z)
  y2 = flowrate q through valve
LC
y=H
Hs
flow in
flow out
MV=z
valve position
WITHOUT CASCADE
WITH CASCADE
measured
flow
LC
y1=H
Hs
flow in
flow out
MV=y2s=qs
FC
y2=q
u=z
master
slave
*Comment: Another approach that uses extra measurements to improve control is «Full state feedback».
Process
U
y1
y2
y1=primary output (given setpoint)
y2=secondary output (adjustable setpoint)

## Slide 9: What are the benefits of adding a flow controller (inner cascade)?
q
z
qs
Counteracts nonlinearity in valve, f(z)
  High gain in inner loop eliminates nonlinearity inside inner loop
  With fast flow control we can assume q = qs
Eliminates effect of disturbances in p1 and p2
(FC reacts faster than outer level loop)
Extra measurement y2 = q
z
(valve opening)
f(z)
0
1
0
1
linear valve

## Slide 10
XC
TC
FC
ys
y
Ls
Ts
L
T
z
XC
Cascade control distillation
3 layers of cascade
With flow loop +
T-loop in top
τc=15s
τc=150s
τc=1500s
=25 min
Problem with many layers:
Eats up the time window

## Slide 11
General case (“parallel cascade”)
Special common case (“series cascade”)
Not always helpful…
y2 must be closely related to y1
Master controller
Slave controller
Master controller
Slave controller

## Slide 12: Block diagram flow controller
Example: Level control with slave flow controller:
u = z (valve position, flow out)
y1 = H
y2 = q
d11 = flow in
di2 = p1-p2
Transfer functions:
G2 = k(z)/(τs+1) where k(z) = dq/dz (nonlinear!)
G1 = - 1/(As)
K1 = Level controller (master)
K2 = Flow controller (slave)
p1
p2
Valve
di1
f(z)
0
1
0
1
linear valve
k(z) = slope df/dz
di2

## Slide 13: Shinskey (1967)

## Slide 14: When use (series) cascade ?
Use cascade control (with an extra secondary measurement y2) when one or more of the following occur:
Significant disturbances d2 and di2 inside slave loop (and y2 can be controlled faster than y1)
The plant G2 is nonlinear or varies with time or is uncertain.
Measurement delay for y1
  Note: In the flowsheet above, y1 is the measured output, so any measurement delay is included in G1
Integrating dynamics (including slow dynamics or unstable) in both G1 and G2, (because without cascade a double integrating plant G1G2 is difficult to control)
Design / tuning
First design K2 (“fast loop”) to deal with d2 and di2 (based on model G2)
Then, with K2 closed, design K1 to deal with d1 and di1 (based on model G1T2)
Slave
controller
Master
controller
di1
di2

## Slide 15: Transfer functions and tuning
T2
d’1
First tune fast inner controller K2 (“slave”)
  Design K2 based on model G2
  Select τc2 based on effective delay in G2
  Transfer function for inner loop (from y2s to y2): T2 = G2 K2/(1+G2 K2)
  Because of integral action, T2 has loop gain = 1 for any G2.
  With SIMC we get: T2 e-ϴ2s/(τc2s+1)
  Nonlinearity: Gain variations (in G2) translate into variations in actual time constant τC2 (see next page)
Then with slave closed, tune slower outer controller K1 (“master”):
  Design K1 based on model G1’=T2*G1
  Can often set T2=1 if inner loop is fast!
  Alternatively, T2 e-ϴ2s/(τc2s+1) e-(ϴ2+τc2)s
  Even more accurate: Use actual T2 (normally not necessary)
  Typical choice: τc1 = τc2 where time scale separation

## Slide 16: Time scale separation is needed for cascade control to work well
Inner loop (slave) should be at least 4 times* faster than the outer loop (master)
  This is to make the two loops (and tuning) independent.
  Otherwise, the slave and master loops may start interacting
    The fast slave loop is able to correct for local disturbances, but the outer loop does not «know» this and if it’s too fast it may start «fighting» with the slave loop.
But recommend 10 times faster,
  A high σ is robust to gain variations (in both inner and outer loop)
  The reason for the upper value (σ =10) is to avoid that control gets too slow, especially if we have many layers
* Shinskey (Controlling multivariable processes, ISA, 1981, p.12)

## Slide 17: Motivation for factor 4 for time scale separation
Response y(t) (lower layer) to step change in setpoint (coming from upper layer):
Lower layer has for any practical purpose converged (98%) after time 4 τc2.

## Slide 18: Counteracting nonlinearity using cascade control
Example: Consider slave flow controller with u = z (valve position) and y2 = q (flow)
  Nonlinear valve with varying gain k2: G2(s)= k2(z) / (s+1)
  Slave (flow) controller K2: PI-controller with gain Kc2 and integral time I= (SIMC-rule). Get
  With slave controller: Transfer function from y2s to y2 (as seen from outer loop):
T2 = L2/(1+L2) = 1/(C2 s + 1), where C2 = /(k2 Kc2)
Linearization: Gain for T2 is always 1 (independent of k2) because of intergal action in the inner (slave) loop
But: Gain variation in k2 (inner loop) translates into variation in closed-loop time constant C2. This may effect the master loop:
  The master controller K1 is designed based on G1T2.
  A smaller process gain k2 results in a larger C2 and thus a large effective delay, whuch mat be bad.
    Recall T2 e-ϴ2s/(τc2s+1) e-(ϴ2+τc2)s
  However, if the time scale separation σ is sufficiently large, the variations in C2 will not matter
f(z)
0
1
0
1
linear valve
k2(z) = slope = df/dz
G1T2 = «Process» for tuning master controller K1

## Slide 19: Cascade control block diagram
Which disturbances motivate the use of cascade control?
C1
C2
P2
P1
+
d2
r1
y1
r2
u
y2
+
d1
+
d1o
Answer: d2

## Slide 20
Example: Similar to shower process
u = Q
y1 = T
d = TF
Simulink model: tunepid1_ex1
Note: level control not explicitly included in simulation (assume constant level)
Looong pipe
µ=100s
¿=20s
Simulink model: tunepid1_ex1

## Slide 21: Disturbance response with no control
y1 = T
Looong pipe
µ=100s
¿=20s
Kc=0; taui=9999; % no control
%start simulation (press green button)
plot(time,u,time,T,time,Tf), axis([0 800 -1.5 1.5])
u = Q
u = Q
y1 = T
d = TF
d = TF

## Slide 22: Conventional PI control (measure y1)
u = Q
y1 = T
d = TF
TC
Ts
No offset, but slow
Kc=0.1; taui=20; % SIMC PI-control
%start simulation (press green button)
plot(time,u,time,T,time,Tf), axis([0 800 -1.5 1.5])

## Slide 23
TC2
T0s
TC
y2=T0
Ts
Measure also y2=T0: Cascade control is much better
Inner slave loop (T0): tauc2=10
Outer master loop (T): tauc=105
Slave controller
(inner loop)
Master controller
(outer loop)
Kc2=0.1;taui2=1; % inner loop with tauc2=10
Kc=0.119; taui=25; % outer loop with tauc=105
sim('tunepid1_ex1_cascade') %start simulation
plot(time,u,time,T,time,Tf,time,T0), axis([0 800 -1.5 1.5])
d = TF
y1 = T
u = Q
G1= exp(-100s)/(20s+1)
G2=1/(s+1)

## Slide 24: Question: Will setpoint tracking for y1 =T be improved with cascade (in this case)?
No, since there was essentially no dynamics in G2=1/(s+1), it is actually slightly worse (tauc increased from 100 to 105).
But if G2 was an integrating process, cascade could improve seytpoint response

## Slide 25: E11. Feedforward (FF) control
Model: y = g u + gd d
Measured disturbance: dm = gdm d
Feedforward controller: u = cFF dm
Get y = (g cFF gdm + gd) d
Ideal feedforward controller:
  y = 0 d -> cFF,ideal = - (gd / (gdm g)
    But often not realizable
  For cFF(s) to be realizable:
      Order pole polynomial cFF ≥ order zero polynomial cFF
      No prediction allowed (µ in cFF cannot be negative)
      And must avoid that CFF has too high gain (to avoid aggressive input changes)
  Common simplification is to use static FF: cFF = k
  General. Approximate cFF,ideal by
g
d
y
u
gd
Measurement
dm
cff
gdm
y
Mainly: For disturbances where feedback control is not good enough.
Note: Feedforward control is model-based.
Since true process is nonlinear, we often include nonlinearity, for example:
  Make k depend on operating point.
  Ratio control
  Nonlinear feedforward control (input transformation)

## Slide 26: When use feedforward?
Recall: cFF,ideal = - gd / (gdm g)
Use FF when
There is an effective delay in the “total process” from u to ym (in gm g) (so that feedback cannot be fast)
  and in particular if there is delay in the measurement of y (gm)
Preferably some “delay” in gd
  Feedforward then has “more time” to take the right action
  Ideally the delay in gd is larger or equal to the delay in gdm g (so cFF,ideal can be realized).
  Note: No delay is needed in gd if the delay in gm is large (because then feedforward always has a potentially large benefit)
And: Have good models
Note: The two yellow measurement transfer functions are not the same.
g
d
y
u
gd
Measurement
dm
cff
gdm
gm
ym
Start week 9

## Slide 27: Example: Similar to shower process
No control
y = T
Looong pipe
µ=100s
¿=20s
u = Q
u = Q
y = T
d = TF (measured)
y2=T0 (yellow)
d = TF
Cff
Kc2=0; % without feedback
Kff=-1 % Feedforward controller, Cff=Kff=-1
sim('tunepid1_ex1_cascade_ff') %start simulation
plot(time,u,"blue",time,T,"green",time,Tf,"red",time,T0,“orange"), axis([0 800 -1.5 1.5])
Feedforward almost perfect (nominal)
(Kff=-1, Kc2=0)
Feedforward with model error
(Change gain in heater from 1 to 1.5)
Cascade with same model error
(Kc2=0.1, Kff=0)
y1
y1
y1
Details: Model heater:
Model pipe and tank:
Nominal: k=1,
Assume perfect measurements: gdm= gm=1
Ideal FF: Cff,ideal = - gd / (gdm g) = = -(s+1)
(more zeros than poles, not realizable)
Simplified: Cff = -1
Conclusion: Feedforward sensitive to model error. Feedback/cascade robust.
gd has delay,
Promising for FF!
Will use Cff = -1 (see details below)
Recall: Cascade (slave for T0) with model error: k=1.5
FF with model error: k=1.5
FF Nominal model: k=1
FF Overcompensates because process gain k increases

## Slide 28: Example 2 FF (extra). Try different simple cFF
g = 5*exp(-2*s)/((3*s+1)*(1.5*s+1)) % Long delay: Feedback alone is not OK
gd = 2*exp(-4*s)/(3*s+1) % Good for FF: even longer delay in gd
gdm = 1/(0.1*s+1)
Disturbance: d=1 occurs at t=0
Desired: y small, u small
cff0 = -0.4*(1.5*s+1)*(0.1*s+1)*exp(-2*s)/(0.001*s+1)2 % Cff,ideal (black)
% Great performance (y=0), but input u much too large!
cff1 = -0.4*exp(-2*s) % Simple. Take away zeros. RED
cff4 = -0.4 % % Even simpler: Static gain. Simplest (green)
% Improvements
cff2 = -0.4*(1.5*s+1)*exp(-2*s)/(0.3*s+1) % Add (1.5s+1) +add filter to cff1, Solid blue
cff3 = -0.4*(1.5*s+1)*exp(-1.7*s)/(0.3*s+1) % Same… but reduce delay when adding filter, dashed blue

## Slide 29
s=tf('s')
gd = 2*exp(-4*s)/(3*s+1)
g = 5*exp(-2*s)/((3*s+1)*(1.5*s+1))
gdm = 1/(0.1*s+1)
cff0 = -0.4*(1.5*s+1)*(0.1*s+1)*exp(-2*s)/(0.001*s+1)^2 % Cff,ideal (black)
cff1 = -0.4*exp(-2*s) % Simple with delay. RED
cff2 = -0.4*(1.5*s+1)*exp(-2*s)/(0.3*s+1) % Add (1.5s+1) + filter, Solid blue
cff3 = -0.4*(1.5*s+1)*exp(-1.7*s)/(0.3*s+1) % Adjust delay, dashed blue
cff4 = - 0.4 % % Simplest (green)
cffno = 0 % % no control
%SIMC PI-controller
theta=2+1.5/2; tau=3+1.5/2; k=5;
tauc=theta;
Kc=(1/k)*(tau/(tauc+theta)), taui=min(tau,3*(tauc+theta))
c = Kc*(1+1/(taui*s));
S=1/(1+g*c);
Td = S*gd; % with PI feedback only
Tdu = -c*S*gd;
T0 = g*cff0*gdm + gd
T1 = g*cff1*gdm + gd
T2 = g*cff2*gdm + gd
T3 = g*cff3*gdm + gd
T4 = g*cff4*gdm + gd
T5 = S*T1 % combine Cff=-0.4 with feedback
Tno = g*cffno*gdm + gd
T0u = gdm*cff0
T1u = gdm*cff1
T2u = gdm*cff2
T3u = gdm*cff3
T4u = gdm*cff4
T5u = S*T1u + Tdu % combine Cff=-0.4 with feedback
Tnou = gdm*cffno
figure(1),step(T0,'black',T1,'red',T2,'blue',T3,'--',T4,'green',T5, 'magenta', Tno,Td), axis([0 20 -0.5 1])
figure(2),step(T0u,'black',T1u,'red',T2u,'blue',T3u,'--',T4u, 'green ', T5u, 'magenta', Tnou,Tdu),axis([0 20 -2 0.5])

## Slide 30
Ideal, cff0
u(t)
cff0 = -0.4*(1.5*s+1)*(0.1*s+1)*exp(-2*s)/(0.001*s+1) % cff,ideal (black) PERFECT y! But Not realistic. TOO LARGE u
cff4 = -0.4 % Simplest: static gain; overcompensates (y in wrong direction) but otwerwise OK (green)
cff1 = -0.4*exp(-2*s) % Add delay. Surprisinlgly, it does not really help compared to cff4 (red)
cff2 = -0.4*(1.5*s+1)*exp(-2*s)/(0.3*s+1) % Add (1.5s+1) + add filter to avoid too large u, Good! (Solid blue)
cff3 = -0.4*(1.5*s+1)*exp(-1.7*s)/(0.3*s+1) % Adjust delay so 1.7+0.3=2. Very good! (BUT with perfect model) (dashed blue)
y(t)
Feedback only
Feedback only
Feedback only is too slow!
All simulations are without model error.
Note simplest case (green line): OK response (compared to feedback only), but y(t) goes in opposite direction initially because it acts too early. This may confuse operators.
MPC may be a better approach in this case (it is generall good for FF)
cff4
cff1
cff2
cff3
No control
(goes to 2)

## Slide 31
Email 11 Dec. 2024
Hei Jose Luis
Yes, what you suggest is reasonable.
Assume we want to find.
Cff = Kff*(Tz*s+1)*exp(-Lff*s) / (Tff*s+1)
Where TFF is the main tuning parameter.
One approach, to make a simple , is to first compiute
CFFideal = (G*Gdm)^-1 Gd
Next, we make a half-rule approximation on Cffideal (to get effective delay) and add a filter
Cff=Cffideal (approximated) w/ filter
Here, Cff (approximated) should have at most one zero, so if there are more then subtract it from the delay (if the delay is large) or from something else-
For the example, we get
Cffideal = -0.4*(1.5*s+1)*(0.1*s+1)*exp(-2*s) \approx -0.4*(1.5*s+1)*exp(-1.9*s)
We have two zeros, so I subtracted the smallest zero from the delay (to get the approximation) – how to do this in general needs more research.
Next, the filter time constant (whenever needed to make a proper CFF) is added. To avoid that makes the FF response worse it should be subtracted from the delay in Cffideal (or added to the zero time constant TZ if there is no delay).
If we end up with a non-realizable negative delay in Cff then it needs to eliminated (and possibly at the same time add it to Tz or subtract it from Tff) .
In our case, the delay is positive
Cff = -0.4*(1.5*s+1)*exp(-D*s)/(Tff*s+1) where D = 1.9 - Tff
And we get with Tff=0.3
Cff = -0.4*(1.5*s+1)*exp(-1.6*s)/(0.3*s+1)
I think this has a good response (not checked, but it’s similar to my previous design).
I think the parts in yellow is different from your present approach? It needs to be considered in more detail….
-Sigurd

## Slide 32
FIX
Example 3
CFF,ideal = - Gd/G = -es
Prediction; not possible, so use
CFF = -1
(SIMC)
For factor B to avoid fighting («overshoot») between FF and FB: see APC course

## Slide 33: Main problem Feedforward (FF): need good models
“If process gain increases by more than a factor 2, then ideal feedforward control is worse than no control”
(makes sense from Shower example! If FF overcompensates too much then it is worse than with no control)
Proof: y = g u + gd d where u=cFF d
Let cFF = - gd/g
Ideal: Get y = g cFF d + gd d = 0
so term “g cFF d” is equal to “-gd d”
Real: If g has increased by a factor x then
y = x(-gd d) + gd d = (-x+1) gd d
And we have that |-x+1| > 1 (worse than no control) for x > 2.
Example: x = 2.1, gd d = 1
  Ideal y = gd d = 1
  Real: y = (-2.1+1)*1 = -1.1 (which is greater than 1 in magnitude, so y overshoots y by more than 1 on the other side)

## Slide 34: Main problem feedforward: Sensitive to model error
“If process gain increases by more than a factor 2, then ideal feedforward control is worse than no control”
  Proof: y = gu + gd d where u=cFF gdm d
  Response with feedforward controller:
  y = (g cFF gdm + gd) d
  Ideal: Use cFF,ideal = - gd/g gdm. Gives y = (-gd + gd) d = 0 d
  But note that g is cFF,ideal is a model
  Real: If the real process gain (g) has increased by a factor x then
  y = (-xgd + gd) d = (-x+1) gd d
  For x>2: |-x+1|>1 (worse than no control)….
  Example, x=2.1, gd=1,
      No control: y = gd d = d
      Ideal: y = 0d
      Real: y = (-2.1+1)*1 = -1.1 d (which is greater than 1 in magnitude, so y overshoots y by more than 1 on the other side…)
This sensitivity to model error justifies why one often includes a “chicken factor” f in feedforward control, cFF = f cFF,ideal , where typically f=0.8.

## Slide 35: Quiz: How can we add feedforward?
LC
CV=H
Hs
d=q1
F2s
FC
F2
z
master
slave

## Slide 36: Solution: How can we add feedforward?
LC
CV=H
Hs
d=F1
F2s
FC
F2
z
master
slave
F1 (measured flow disturbance)
(F2-F1)s
+

## Slide 37: E2. Ratio control (most common case of feedforward)
x
(F2/F1)s
(desired flow ratio)
F1
(measured
flow disturbance)
F2
(Input, manipulated variable)
“Measure disturbance (d=F1) and adjust input (u=F2) such that
ratio is at given value (F2/F1)s”
Use multiplication block (x):
Note: Disturbance needs to be a flow (or more generally an extensive variable)
Very common when a unit has several feed streams.
Example: Process with two feeds F1(d) and F2 (u), where ratio should be constant.
Don’t need a model; just need process insight (about when it can be used)

## Slide 38: Usually: Combine ratio (feedforward) with feedback
Adjust (F1/F2)s based on feedback from process, for example, composition controller.
    This is a special case of cascade control
  Example cake baking: Use recipe (ratio control = feedforward), but adjust ratio if result is not as desired (feedback)
  Example evaporator: Fix ratio qH/qF (and use feedback from T to fine tune ratio)

## Slide 39
Flour
(solid)
Want to control: Viscosity y [cP]
(or any intensive quality variable, like c, ρ or T)
y
∞
Product
Water
FC
x
R=(F2/F1)s
u= F2,s
d=F1,m
F2,m
VC
ym
ys
RATIO CONTROL
with outer feedback (to adjust ratio setpoint)
EXAMPLE: CAKE BAKING MIXING PROCESS
Note : This way of implementing ratio control makes it easy to tune the outer feedback loop (here: VC) because the gain from MV = Rs= (F2/F1)s to CV=y (here: viscosity) does not depend on the flowrate (that is, it is independent of disturbances in F1).
Feedback correction («trim»)

## Slide 40: Ratio control
Avoid divisions in implementation! (can divide by 0)
Book has some strange suggestions, for example, Figure 14.5
Bad solution
Avoid divisions (divide by 0 if u =0, for example, at startup)
This is complicated. What is RS?
Ok if implemented as shown in red at right

## Slide 41: Valve position control (VPC)
Have extra MV (input): One CV, many MVs
Process
Two different cases of VPC:
E3. Have extra dynamic MV
  Both MVs are used all the time
E7. Have extra static MV
  May use VPC for MV-MV switching: see later

## Slide 42: E3. VPC for extra dynamic input
Alternative term for dynamic VPC:
Mid-ranging control (Sweden)
u2 = main input for steady-state control of CV
(but u2 is poor for directly controlling y
  e.g. time delay or u2 is on/off )
u1 = extra dynamic input for fast control of y
VPC
Process
u1
u2
y
Example 1: Large (u2) and small valve (u1) (in parallell) for controlling total flowrate (y=F)
  The large valve (u2) has a lot of stiction which gives oscillations if used alone for flow control
  The small valve (u1) has less stiction and gives good flow control, but it’s too small to use alone
Example 2: Strong base (u2) and weak base (u1) for neutralizing acid (disturbance) to control y=pH
  Do pH change gradually (in two tanks) with the strong base (u2) in the first tank and the weak base (u1) in the last tank. u1 controls the pH in the last tank (y)

## Slide 43: Example: Heat exchanger with bypass
Want tight control of y=T.
u1=zB (bypass)
u2=CW
Proposed control structure?
zB
T

## Slide 44: Attempt 1. Use u2=cooling water: TOO SLOW
zB=0 (closed)
T
TC

## Slide 45: Attempt 2. Use u1=zB=bypass. SATURATES (at zB=0=closed if CW too small)
T
TC
=constant
zB
Advantage: Very fast response (no delay)
Problem: zB is too small to cover whole range
+ not optimal to fix at large bypass (waste of CW)

## Slide 46: What about VPC?
Want tight control of y=T.
u1= zB
u2=CW
Proposed control structure?
Main control: u2=CW
Fast control: u1=zB
zB
T

## Slide 47: Attempt 3 (proposed): VPC
T
TC
zB
SP=50%
VPC
Fast control of y: u1 = zB
Main control (VPC): u2=CW (slow loop)
Need time scale separation between the two loops

## Slide 48: Alternative to VPC: Parallell control

## Slide 49: Standard Advanced control elements
Each element links a subset of inputs with a subset of outputs
Results in simple local tuning
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages).