## Slide 1: Multivariable control
Single-loop control (decentralized)
Decoupling (similar to feedforward)
Model predictive control (MPC)

## Slide 2: I. Multivariable control using single loops
Pairing rules
Interactions
Choice of pairings (RGA)

## Slide 3
MVs: u = (qh qc)
CVs: y = (T q)
What pairing?

## Slide 4: Which input (MV) to pair with a given output (CV)? Two main pairing rules (based on process insight):
“Pair-close rule”
  The MV should have a large, fast, and direct effect on the CV
  Sometimes not obvious:
    RGA may help for selecting pairing
    or use multivariable control
“Input saturation rule”
  Pair a MV that may saturate with a CV that can be given up (when the MV saturates)
Process
MV
CV
DV

## Slide 5: Shower example, MV=(qh qc), CV= (T q)
“Pair-close rule: The MV should have a large, fast, and direct effect on the CV”
  Shower, Rule 1:
    Use largest flow (of qc and qh) for flow control
    and smallest flow for temperature control
“Input saturation rule: Pair a MV that may saturate with a CV that can be given up (when the MV saturates)”
  Shower: Assume hot water (qh) may saturate (at fully open) and that flow control can be given up (it’s most important is to control temperature). Rule 2 gives:
    Use hot water for flow control
      Give up flow control if hot water saturates at max
    Use cold water (qh) for temperature control
But shower is very coupled, so maybe we need decoupling

## Slide 6: Multivariable process
Distillation column
“Increasing reflux L from 1.0 to 1.1 changes yD from 0.95 to 0.97, and xB from 0.02 to 0.03”
“Increasing boilup V from 1.5 to 1.6 changes yD from 0.95 to 0.94, and xB from 0.02 to 0.01”
Steady-State Gain Matrix
(Time constant 50 min for yD)
(time constant 40 min for xB)

## Slide 7: Analysis of Multivariable processes
INTERACTIONS: Caused by nonzero offdiagonal elements (g12 and/or g21)
Process Model 2x2
y1
y2
g12
g21
g11
g22
u2
u1
(1)
(2)

## Slide 8: RGA: Consider effect of u1 on y1
“Open-loop” (C2 = 0): y1 = g11(s)·u1
“Closed-loop” (close loop 2, C2≠0):
Change caused by “interactions”
C2
y1
y2
g12
g21
g11
g22
u2
u1
Misprint: g11 should be inside parahthesis (

## Slide 9
Limiting Case C2→∞ (perfect control of y2) *
How much has “gain” from u1 to y1 changed by closing loop 2 with perfect control?
The relative Gain Array (RGA) is the matrix formed by considering all the relative gains

## Slide 10
Example from before

## Slide 11
Interactions
  RGA-element ()> 1: Smaller gain by closing other loops (“fighting loops” gives slower control)
  RGA-element () <1: Larger gain by closing other loops (can get instability when other loop is closed)
  RGA-element () negative: Gain reversal by closing other loops (Oops!)
Use of RGA:
Rule 2. Choose pairings corresponding to RGA-elements close to 1
Traditional: Consider Steady-state
Better (improved Rule 2): Consider frequency corresponding to closed-loop time constant
Rule 1. Avoid pairing on negative steady-state relative gain – otherwise you get instability if one of the loops become inactive (e.g. because of saturation)

## Slide 12: Example 3x3 process: 6 possible pairing options
Only diagonal pairings give positive steady-state RGA’s!

## Slide 13
Property of RGA:
Columns and rows always sum to 1
RGA independent of scaling (units) for u and y.
>> rga=G.*pinv(G).'
rga =
0.3125 1.2500 -0.5625
1.2500 -0.2500 0
-0.5625 0 1.5625
G = [5 10 1; 20 -10 0; 18 0 2]
G =
5 10 1
20 -10 0
18 0 2
Example
Conclusion: of the 6 possible pairings only one has positive RGA’s

## Slide 14
TC
T
s
Distillation

## Slide 15
TC
T
s
TC
T
s
TC
T
s
Resulting RGA with temperature control:
K
c
=0
0.1
1
Distillation
Can break interactions with cascade:
Frequency-dependent RGA with TC
35

## Slide 16: Sometimes useful: Iterative RGA
For large processes, lots of pairing alternatives
RGA evaluated iteratively is helpful for quick screening
Converges to “Permuted Identity” matrix (correct pairings) for generalized diagonally dominant processes.
Can converge to incorrect pairings, when no alternatives are dominant.
Usually converges in 5-6 iterations

## Slide 17: Example of Iterative RGA
Correct pairing

## Slide 18: Exercise. Blending process (or shower)
Mass balances (no dynamics)
  Total: F1 + F2 = F
  Sugar: F1 = x F
Linearize balances and introduce: u1=dF1, u2=dF2, y1=F1, y2=x,
Obtain gain matrix G (y = G u)
Nominal values are x=0.2 [kg/kg] and F=2 [kg/s]. Find G
Compute RGA and suggest pairings
Does the pairing choice agree with “common sense”?
sugar u1=F1
water u2=F2
y1 = F (given flowrate)
y2 = x (given sugar fraction)

## Slide 20: Decentralized control tuning
Independent design of each controller
  Use when small interactions (RGA close to I)
Sequential design (similar to cascade)
  Start with fast loop
  NOTE: It’s possible to pair on negative RGA, but then system will go unstable if the inner loop is not active (saturates)
  Sequential vs. independent design
    + Sequential may have better performance, but
    - outer loop gets slow, and
    - loops depend on each other

## Slide 21: Summary Single-loop control = Decentralized control
Use for: Noninteracting process
+ Tuning may be done on-line
+ No or minimal model requirements
+ Easy to fix and change
- Need to determine pairing
- Performance loss compared to multivariable control

## Slide 22: Breaking interactions with cascade control (fast slave loop)
Example 1. Control of level and pressure in separator
MVs: Valve positions for liquid and gas out
Highly interactive
Interactions can be avoided with cascade! How?
Example 2. Control of compositions in distillation column
MVs: Reflux and heat input (boilup)
Time delay on composition measurements
Highly interactive
Can to some extent be avoided with cascade (inner temperature loop)

## Slide 23: Multivariable control
Single-loop control (decentralized)
Decoupling (similar to feedforward)
Model predictive control (MPC)

## Slide 24: II. Decoupling a) One-way Decoupling (improved control of y1)
c2
g11 g12
g21 g22
y1
y2
r1-y1
r2-y2
u2
u1
c1
DERIVATION
Process: y1 = g11 u1 + g12 u2 (1)
y2 = g21 u1 + g22 u2 (2)
Consider u2 as disturbance for control of y1.
Think «feedforward»: Adjust u1 to make y1=0. (1) gives u1 = - (g12/g11) u2
-g12/g11
one-way coupled process
D12

## Slide 25: b) Two-way Decoupling: Standard implementation (Seborg)
c2
g11 g12
g21 g22
y1
y2
r1-y1
r2-y2
u2
u1
c1
… but note that diagonal elements of decoupled process are different from G
Problem for tuning!
Process: y1 = g11 u1 + g12 u2
Decoupled process: y1 = (g11-g12*g21/g22) u1’ + 0*u2’
Similar for y2.
-g12/g11
-g21/g22
decoupled process = ([G-1]diag)-1
u’1
u’2

## Slide 26: Two-way Decoupling: «Inverted» implementation (Shinskey)
c2
g11 g12
g21 g22
y1
y2
r1-y1
r2-y2
u2
u1
c1
-g12/g11
-g21/g22
decoupled process= Gdiag
u’1
Advantages: (1) Decoupled process has same diagonal elements as G. Easy tuning!
(2) Handles input saturation! (if u1 and u2 are actual inputs)
Proof (1): y1 = g11 u1 + g12 u2, where u1 = u1’ – (g12/g11)u2.
Gives : y1 = g11 u’1 + 0* u2’
Similar: y2 = 0*u1’ + g22 u2’
u’2
Sigurd recommends this alternative!
See Exercise

## Slide 27: Pairing and decoupling
To get ideal decoupling, diagonal elements should have smaller effective delay than the off-diagonal elements
Thus, we should pair on elements with small effective delay (“pair close rule”)
  This is usually achieved if we follow the “normal” RGA-rules of pairing on elements as close to 1 as possible.

## Slide 28: Nonlinear decoupling and feedforwrd
Linear decoupling and feedforward often work poorly because of nonlinearity
Example of nonlinear feedforward: Ratio control
It’s often easier to make nonlinear decoupler / feedforward based on static model or insight

## Slide 29: Example decoupling: Mixing of hot (u1) and cold (u2) water
Want to control
  y1 = Temperature T
  y2 = total flow F
Inputs, u=flowrates
May use two SISO PI-controllers
  TC
  FC
Insight: Get decoupled response with transformed inputs
  TC sets flow ratio, v1 = u1/u2
  FC sets flow sum, v2 = u1 + u2
Decoupler: Need «static calculation block» to solve for inputs
u1 = v1 v2 / (1+ v1)
u2 = v2 / (1 + v1)
T
F
u1
u2
v2=sum
v1=ratio

## Slide 30: «Transformed inputs» v
Combining feedforward with feedback in an extremely simple way
Most effective for static feedforward
  Dynamic generalzation (= «feedback linearization») usually unrealistic because of many derivatives
Static model: y =f(u,d)
Select transformed inputs (= controller outputs): v = f(u,d)
Invert to get physical inputs: u = f-1(v,d)
Then response from v to y is: y= I v (linear, decoupled, perfect disturbance rejection)
FeedbackController
Calculation block (static FF)
Process
ys
y
V
d
u
y

## Slide 31
Controller
Calculation block (static)
Process
ys
y
V
d
u
y
TRANSFORMED INPUTS v: GENERAL APPROACH FOR COMBINED FEEDBACK,
FEEDFORWARD, DECOUPLING AND LINEARIZATION
Example: Mixing of hot and cold water
Generalized ratio
Decoupler with feedforward:
It’s almost magic!

## Slide 32: V. Pole placement (state feedback using P-only control)
Place closed-loop poles. Old design method
Useful for insight, but difficult to choose K. Not used much in practice, at least not for linear controllers
Basis:
  Linear system on state space form
  and use “State feedback” P-control (assuming we can measure all the states)
Note
SIMC is “pole placement” (p=-1/tauc), but with output feedback (y), and we also place zeros
If we cannot measure all the states, then we can estimate x from y using a “Kalman filter”.
State feedback uses extra measurements – an alternative is cascade control
dx/dt = A x + B u

## Slide 35: MPC

## Slide 36: Advanced multivariable control with explicit constraint handling = MPC
Use for: Interacting process and changes in active constraints
+ Easy handling of feedforward control
+ Easy handling of changing constraints
    no need for logic
    But does not always work
- Requires multivariable dynamic model
- Tuning may be difficult
Less transparent; not clear how it handles a given situatiion
Used if “conventional advanced control” is not good enough
  Typically implemented after some time of operation (more than one year)
- “Everything goes down at the same time”
MPC = model predictive control

## Slide 37: Multivariable control: MPC versus (linear) decoupling
Both MPC and decoupling require a multivariable process model
MPC is usually preferred instead of decoupling because it can also handle feedforward control, nonsquare processes (cascade, input resetting) dynamic, etc.
MPC can also handle constraints
  Has “built-in” anti-windup
MPC = Model predictive control

## Slide 38: Model predictive control (MPC) = “online optimal control”
Note: Implement only current input Δu1
ydev=y-ys
udev=u-us
Discretize in time:

## Slide 39: Implementation MPC project (Stig Strand, Equinor)
Initial MV/CV/DV selection
DCS* preparation (controller tuning, instrumentation, MV handles, communication logics etc)
Control room operator pre-training and motivation
Product quality control  Data collection (process/lab)  Inferential model (“soft sensor”)
MV/DV step testing  dynamic models
Model judgement/singularity analysis  remove models? change models?
MPC pre-tuning by simulation  MPC activation – step by step and with care – challenging different constraint combinations – adjust models?
Control room operator training
MPC in normal operation, with at least 99% service factor
*DCS = “distributed control system” = Basic PID control layer

## Slide 40
Depropaniser Train 100 – 24-VE-107
21
1
5
6
17
20
33
34
39
48
35
40
18
24
TC
1022
LP condensate
LP steam
24
LC
1026
24
PC
1010
24
TI
1018
24
LC
1009
24-HA-103
A/B
24-VA-102
24-PA-102A/B
24
FC
1008
24
TI
1021
24
LC
1010
24
TI
1038
24
TI
1020
24
PC
1020
24
PDC
1021
24
HC
1015
Kjølevann
24-VE-107
24
TI
1011
24
TI
1017
24
TI
1012
24
PI
1014
24
PD
1009
24
FC
1009
24
TI
1013
Propane
Flare
Bottoms from deetaniser
25
FI
1003
2 Manipulated variables (MV) = Set points to PID controllers
24
TI
1005
24
LC
1001
24LC1001.VYA
1 Disturbance variable (DV) = Feedforward
24
AR
1005
C = C3
E = nC4
F = C5+
Debutaniser 24-VE-108
24
AR
1008
B = C2
C = C3
D = iC4
3 Controlled variables (CV) = Product qualities, column deltaP
Normally 0 flow, used for start-ups to remove inerts
CV1=xD
CV3=DP
CV2=xB
MV1=L
MV2=Ts
DV=F

## Slide 41
Conventional control (PID)
Select pairings MV-CV (obvious here: L-xD, Ts-xB)
Selector: Give up xB when we meet DP constraint
Tune 3 PI controllers

## Slide 42
Depropaniser Train 100 – 24-VE-107
21
1
5
6
17
20
33
34
39
48
35
40
18
24
TC
1022
LP condensate
LP steam
24
LC
1026
24
PC
1010
24
TI
1018
24
LC
1009
24-HA-103
A/B
24-VA-102
24-PA-102A/B
24
FC
1008
24
TI
1021
24
LC
1010
24
TI
1038
24
TI
1020
24
PC
1020
24
PDC
1021
24
HC
1015
Kjølevann
24-VE-107
24
TI
1011
24
TI
1017
24
TI
1012
24
PI
1014
24
PD
1009
24
FC
1009
24
TI
1013
Propane
Flare
Bottoms from deetaniser
25
FI
1003
24
TI
1005
24
LC
1001
24LC1001.VYA
24
AR
1005
C = C3
E = nC4
F = C5+
Debutaniser 24-VE-108
24
AR
1008
B = C2
C = C3
D = iC4
Normally 0 flow, used for start-ups to remove inerts
CV1=xD
CV3=DP
CV2=xB
MV1=L
MV2=Ts
DV=F
DPC
MAX
DPmax
Conventional control: selector when DP>DPmax
Here selector on MV from TC.
Could have selector on Ts instead

## Slide 43
Depropaniser Train 100 – 24-VE-107
21
1
5
6
17
20
33
34
39
48
35
40
18
24
TC
1022
LP condensate
LP steam
24
LC
1026
24
PC
1010
24
TI
1018
24
LC
1009
24-HA-103
A/B
24-VA-102
24-PA-102A/B
24
FC
1008
24
TI
1021
24
LC
1010
24
TI
1038
24
TI
1020
24
PC
1020
24
PDC
1021
24
HC
1015
Kjølevann
24-VE-107
24
TI
1011
24
TI
1017
24
TI
1012
24
PI
1014
24
PD
1009
24
FC
1009
24
TI
1013
Propane
Flare
Bottoms from deetaniser
25
FI
1003
24
TI
1005
24
LC
1001
24LC1001.VYA
24
AR
1005
C = C3
E = nC4
F = C5+
Debutaniser 24-VE-108
24
AR
1008
B = C2
C = C3
D = iC4
Normally 0 flow, used for start-ups to remove inerts
CV1=xD
CV3=DP
CV2=xB
MV1=L
MV2=Ts
DV=F
DPC
MAX
DPmax
Conventional control: selector when DP>DPmax
Here selector on MV from TC.
Could have selector on Ts instead
CC2
CC1

## Slide 44
Conventional control (PID)
Select pairings MV-CV (obvious here: L-xD, Ts-xB)
Selector: Give up xB when we meet DP constraint
Tune 3 PI controllers (CC1, CC2, DPC)
MPC
Don’t need to make pairing choices
But need model
And need to tune MPC controller

## Slide 45
Depropaniser Train100 step testing
3 days – normal operation during night
CV1=TOP COMPOSITION
CV2=BOTTOM COMPOSITION
CV3=¢p
DV =Feedrate
MV1 = L
MV2 = Ts

## Slide 46
Estimator: inferential models
Analyser responses are delayed – temperature measurements respond 20 min earlier
Combine temperature measurements  predicts product qualities well
Calculated by 24TI1011 (tray 39)
Calculated by 24TC1022 (t5), 24TI1018 (bottom), 24TI1012 (t17) and 24TI1011 (t39)
CV1=TOP COMPOSITION
CV2=BOTTOM COMPOSITION

## Slide 47
Depropaniser Train100 step testing – Final model
Step response models:
  MV1=reflux set point increase of 1 kg/h
  MV2=temperature set point increase of 1 degree C
  DV=output increase of 1%.
3 t 20 min
MV2 = Ts
MV1 = L
DV =Feedrate
CV1=TOP COMPOSITION
CV2=BOTTOM COMPOSITION
CV3=Δp

## Slide 48
Depropaniser Train100 MPC – controller activation
Starts with 1 MV and 1 CV – CV set point changes, controller tuning, model verification and corrections
Shifts to another MV/CV pair, same procedure
Interactions verified – controls 2x2 system (2 MV + 2 CV)
Expects 3 – 5 days tuning with set point changes to achieve satisfactory performance
MV1 = L
MV2 = Ts
DV =Feedrate
CV1=TOP COMPOSITION
CV2=BOTTOM COMPOSITION
CV3=Dp

## Slide 49
Reflux drum
Reflux pumps
21
20
1
10
16
23
28
34
Heat ex
PC
Propane
Product pumps
LC
TC
To Depropaniser
LP Condensate
LP Steam
Feed from stabilizators
FC
Flare
0 – 65%
65-100%
FC
FC
FC
LC
PC
Fuel gas
to boilers
CV
CV
CV
MV
MV
DV
Another column:
Deethanizer
Quality estimator
Quality estimator
LC
Notes: One example of using MPC at the column level.
What do we want to control? Product quality + avoid flaring
Bias update from analyzators

## Slide 50: Top: Binary separation in this case Quality estimator vs. gas chromatograph (use logarithmic composition to reduce nonlinearity, CV = - ln ximpurity)
7 temperatures
2 temperatures
=little difference if the right temperatures are chosen

## Slide 51: The final test: MPC in closed-loop
CV1
CV2
CV3
MV1
MV2
DV

## Slide 52: Conclusion MPC
Sometimes simpler than previous advanced control
Well accepted by operators
Equinor: Use of in-house technology and expertise successful