## Slide 1: Crash course process control
Sigurd Skogestad
Institutt for kjemisk prosessteknologi
(Department of Chemical Engineering)
Room K4-211
skoge@ntnu.no
TexPoint fonts used in EMF.
Read the TexPoint manual before you delete this box.: AAAAAAA

## Slide 3
Course for 3rd year students:
Pensum (syllabus): Lectures/exercises
  Literature (see www.nt.ntnu.no/users/skoge/prosessregulering_lynkurs):
  1. Nybraaten og Svendsen, "Kort innføring i prosessregulering" (1986)
  (det kan synes gammelt, men det står faktisk mye bra her)
  2. 12 sider fra F. Haugen, "Anvendt reguleringsteknikk", 1992
  3. S. Skogestad, "Prosessteknikk", 2./3. utgave, Tapir: Kap. 11.3 (tidsrespons) og 11.8/11.6 (prosessregulering)
  3. S. Skogestad, ”Chemical and Energy Process Engineering”, CRC Press, 2009: Ch. 11.3 (Dynamic analysis and time response) + Ch. 11.6 (Process control)
  Slides
Forelesningsplan
F1: Oversikt over regulering, forover- og tilbakekobling, dusjeksempel
F2: Klassifisering av variable, prosedyre for utforming av reguleringssystem
F3: Eksempler
F4: Prosessdynamikk, tidskonstant, dødtid, PID-regulering,
F5/F6: Stabilitet, Tuning PID, Forsøk, Eksempler,
More information (literature, old exams, etc.):
www.nt.ntnu.no/users/skoge/prosessregulering_lynkurs

## Slide 4
English | Norsk | English | Norsk
Control | regulering |  | 
Operation | drift | Loop | Sløyfe
Measurement (process value, PV) | måling | Valve | Ventil
Disturbance DV | forstyrrelse | Gain | Forsterkning
Manipulated var. (MV) = input | Pådrag = inngang | Time delay = dead time (θ) | Tidsforsinkelse = dødtid (θ)
Controlled variab. (CV) = output | Regulert variabel = utgang |  | 
Feedback | Tilbakekobling |  | 
Feedforward | Foroverkobling |  | 
Controller | Regulator |  | 

## Slide 5: Why control?
Until now: Design of process. Assume steady-state
Now: Operation
time
Actual value(dynamic)
Steady-state (average)
In practice never steady-state:
  Feed changes
  Startup
  Operator changes
  Failures
  …..
Control is needed to counteract disturbances – remain at steady state
30% of investment costs are typically for instrumentation and control
“Disturbances” (d’s)

## Slide 6: Dealing with disturbances. Three approaches:
  1. Design process so it’s insensitive to disturbances
      Example: Use buffer tank to dampen (smoothen) disturbances
  2. Detect and remove the source of disturbances
      Sometimes called “statistical process control” (SPC)
        But it’s not control in our sense of the word
      Example: Detect and eliminate variations in feed (e.g., by using better quality raw material)
  3. Counteract disturbances using MV (this course). MV = manipulated variable (usually valve)
Tin
inflow
outflow
∞
Tout

## Slide 7: 3. Counteract disturbances (this course). Process control (“prosessregulering”):
Do something (usually manipulate valve)
to counteract the effect of the disturbances
  (a) Manual control: Need operator
  (b) Automatic control: Need measurement + automatic valve + computer
    Goals automatic control:
      Smaller variations
        more consistent quality
        More optimal (“squeeze and shift”)
      Smaller losses (environment)
      Lower costs
      More production
    Industry: Still large potential for improvements!

## Slide 8: Motivation for better control: Squeeze and shift rule
y
By improving control and squeezing the variation
we can shift the setpoint (average) closer to the constraint (that is, reduce the back-off)
and increase production

## Slide 9: Example: Control of shower temperature
(valves)
Temperature: 5s delay in pipe (θ = V/q = 100ml/20 ml/s = 5s)
T [K]
q [m3/s]
want constant
Disturbance: Room mate brushes teeth (uses cold water)
Potential problem with
feedback control:
Delay + impatient (“high gain”)
-> Overreact -> Instability
Time delay θ is the main enemy of feedback control
qC[m3/s]
qH

## Slide 10: Classification of variables
Process
(shower)
u
input (MV)
y
output (CV)
d
Independent variables (“the cause”):
  Inputs (MV, u): Variables we can adjust (valves)
  Disturbances (DV, d): Variables outside our control
Dependent (output) variables (“the effect or result”):
  (c) Primary outputs (CVs, y): Variables we want to keep at a given setpoint ys
  (d) Secondary process variables (y2) , Internal variables in dynamic model (“states”) (x)
MV = manipulated vartiable (input u)
CV = controlled variable (output y) (sometimes called PV=process variable)
DV = disturbance variable (d)

## Slide 11: Classification of variables: Shower process
5s delay: θ = V/q = 100ml/20 ml/s = 5s
qC[m3/s]
qH
T [K]
q [m3/s]
Control objective
  Keep temperature (y1=T) a given setpoint
  Keep total flow (y2=q) at given setpoint
2. Classify variables
  MVs (u) = qH, qC (strictly speaking, valve positions zH, zC)
  CVs (y) = T, q
  DVs (d) = qH, qC (strictly speaking, upstream pressures,
  pH, pC, which gives “uncontrolled” flow changes)
Control objective. MVs, CVs, DVs

## Slide 12: Inputs for control (MVs)
Usually: Inputs (MVs) are valves.
  Physical input is valve position (z), but we often simplify and say that flow (q) is input
DP = pressure drop across valve [N/m2]
f(z) = valve characteristic (Linear valve: f(z)=z)
Cv = valve constant [m2] = Cd A (A [m2] = valve area, Cd (typical))
ρ = fluid density [kg/m3]
Start lecture 2

## Slide 13: Control
Use inputs (MVs, u) to counteract the effect of the disturbances (DVs, d) such that the outputs (CVs, y) are kept close to their setpoints (ys)
Process
u
input (MV)
y
output (CV)
d

## Slide 14: Two fundamental control principles
Feedback: Measure the result (= controlled variable CV; output y) and keep adjusting the manipulated variable (MV; input u) until the results is OK
  Example: Measure the temperature y=T (CV) and adjust the flow (u) of cold water (MV)
Feedforward: Measure the cause (= disturbance d; DV) and based on a prediction (model!) make a ”feedforward” adjustment of the MV (input u) to (hopefully) counteract its effect on the result (output y)
  Feedforward control requires a good model!
  Example: Room mate (disturbance d) says ”I am tapping cold water” - and you know your friend so well (model) that you can make the correct increase in your cold water (MV) to counteract d.
  NOT VERY REALISTIC FOR SHOWER EXAMPLE
  BUT a good example of feedforward is coming in time to lecture!
Process
u
input (MV)
y
output (CV)
d

## Slide 15: BLOCK DIAGRAMS
Controller
(brain)
Measurement
device
ys
Desired value
Setpoint
ys-ym
error
ym
measured output
FEEDBACK (measure output):
Process
(shower)
u
input (MV)
y
output (CV)
d
Controller
(brain)
Process
(shower)
Measurement
device
FEEDFORWARD (measure disturbance):
dm
measured disturbance
d
u
input (MV)
y
output (CV)
All lines: Signals (information)
Blocks: controllers and process
Do not confuse block diagram (lines are signals) with flowsheet (lines are flows); see below

## Slide 16
FEEDBACK
  + Self-correcting with negative feedback (keeps adjusting until y=ys at steady state)
  + Do not need good model (but must know process sign!)
  - May give instability if controller overreacts
  Need good and fast measurement of output
  MAIN ENEMY OF FEEDBACK: TIME DELAY
  (in process or in measurement of y)
  USUALLY COMBINED WITH FEEDBACK
FEEDFORWARD
  + Consider when large time delay (in process or in measurement of y)
  + May react before damage is done
  Need good model
  Sensitive to changes and errors
  Works only for known and measured disturbances

## Slide 17: We use two kind of diagrams
Block diagram (information)
  Used by control engineers
Flowsheet (piping & instrumentation diagram, P&ID)
  Used by process engineers

## Slide 18: Piping and instrumentation diagram (P&ID) (flowsheet)
Solid lines: mass flow (streams)
Dashed lines: signals (control)
Example: Shower
mixer
pipe
TC
T
Ts
qC
qH
.
FC
qs
q
valves

## Slide 19: Notation feedback controllers (P&ID)
TC
2nd letter:
C: controller
I: indicator (measurement)
T: transmitter (measurement)
A: alarm
1st letter: Controlled variable (CV) = What we are trying to control (keep constant)
T: temperature
F: flow
L: level
P: pressure
DP: differential pressure (Δp)
A, C: Analyzer (composition) (can also have self-defining symbols like CO2, pH, etc.)
D: density
M: moisture
E: enthalpy/energy
V: viscosity
H: Hand control (manual operation of valve)
Ts
(setpoint CV)
T
(measured CV)
MV (could be valve)

## Slide 20
H
Inflow (u)
Outflow (d)
INPUT (u, MV): INFLOW
OUTPUT (y, CV): LEVEL
DISTURBANCE (d, DV): OUTFLOW
LC
Hs
CLASSIFICATION OF VARIABLES FOR CONTROL (MV, CV, DV):
Example flowsheet: Level control
(with given outflow)

## Slide 21
LC
H
Hs
Inflow (d)
Outflow (u)
INPUT (u, MV): OUTFLOW (Input for control!)
OUTPUT (y, CV): LEVEL
DISTURBANCE (d, DV): INFLOW
CLASSIFICATION OF VARIABLES FOR CONTROL (MV, CV, DV):
Level control when inflow is given
(more common)

## Slide 22: Example: Evaporator with heating
From
reactor
qF [m3/s]
TF [K]
q [m3/s]
T [K]
qH [m3/s]
TH [K]
Heating fluid
evaporation
level measurement
temperature measurement
T
∞
H
Control objective
  Keep level H at desired value
  Keep temperature T at desired value
Classify variables (CVs, MVs, important DVs)
Qualitative model: Process matrix (+-0 from MVs to CVs) to help with pairings and sign of controller gain (Kc)
Suggest pairings and put control loops on the flowsheet
concentrate
 | Input 1 q (outflow) | Input 2 qH
Output 1 H |  | 
Output 2 T |  | 
- -
0 +
Suggested pairings
Avoid pairing on zero gain (otherwise you will depend on other loops being closed)

## Slide 23: Most important control structures
Feedback control
Cascade control
Ratio control (special case of feedforward, but needs no model)
The last two are used if standard feedback is not good enough, typically because of delay in measurement of y.
  Cascade: Use extra output measurement (y2)
  Ratio/feedforward: Use disturbance measurement (d)
2024: Start lecture 3

## Slide 24: Cascade control
Primary Controller (“master”) gives setpoint to a secondary controller (“slave”)
  Without cascade: “Master” controller directly adjusts u (input, MV) to control y
  With cascade: Local “slave” controller uses u to control “extra”/fast measurement (y2).
  “Master” controller adjusts setpoint y2s.
Example: Flow controller on valve (very common!)
  y = level H in tank (or could be temperature etc.)
  u = valve position (z)
  y2 = flowrate q through valve
LC
y=H
Hs
flow in
flow out
MV=z
valve position
WITHOUT CASCADE
WITH CASCADE (2 controllers)
measured
flow
LC
Hs
flow in
flow out
MV=qs
FC
y2=q
MV2=z
master
slave
measured
level
measured
level
y=H

## Slide 25: What are the benefits of adding a flow controller (inner cascade)?
q
z
qs
Fast local control: Eliminates effect of disturbances in p1 and p2
(FC reacts faster than outer level loop)
2. Counteracts nonlinearity in valve, f(z)
  With fast flow control we can assume q = qs
Extra measurement y2= q
f(z)
z
(valve opening)
0
1
0
1
linear valve

## Slide 26: Example: Evaporator with heating
Feed: From
reactor
qF [m3/s]
TF [K]
cF [mol/m3]
q [m3/s]
T [K]
c [mol/m3]
Heating fluid
qH [m3/s]
TH [K]
evaporation
level measurement
temperature measurement
T
∞
H
Control objectives
  Keep level H at desired value
  NOW: Keep composition c at desired value
BUT: Composition measurement has large delay + unreliable
Suggest control structure based on cascade control
Concentrated product
T
concentration measurement
c

## Slide 27: Ratio control
x
(q2/q1)s
(desired flow ratio)
q1
(measured
flow
disturbance)
q2
(MV: manipulated variable)
“Measure disturbance (d=q1) and adjust input (u=q2) such that
ratio is at given value (q2/q1)s”
Use multiplication block (x):
Special case of feedforward (the most common one)
It actually does not require a model, just physical insight!
VERY common for mixing
Example: Process with two feeds q1(d) and q2 (u), where ratio should be constant.

## Slide 28: Usually: Combine ratio (feedforward) with feedback
Adjust (q1/q2)s based on feedback from process, for example, composition controller.
    This is a special case of cascade control
  Example cake baking: Use recipe (ratio control = feedforward), but adjust ratio if result is not as desired (feedback)
  Example evaporator: Fix ratio qH/qF (and use feedback from y=c to fine tune ratio)

## Slide 29
Concentrate
q1 [m3/s]
C1 [mol/m3]
q [m3/s]
c [mol/m3]
c
∞
H
Diluted product
LC
C2=0
Water
FC
x
(q2/q1)s
q2,s
q1,m
q2,m
CC
cm
cs
RATIO CONTROL
with outer cascade (to adjust ratio setpoint)
EXAMPLE: MIXING PROCESS

## Slide 30: Procedure for design of control system
Define control objective (why control?)
Classify variables
    CVs (y)
    MVs (u)
    Disturbances (d)
    + measurements
Process description
    Flow sheet
    Model: Process matrix
      - Qualitative: with 0, +, -, (+)*, (-)*
      - Quantitative: transfer matrix (see later)
Control structure
    Feedback
      Pairing of variables (avoid pairing on 0!)
    Cascade loops (MV from one controller (master) is setpoint for another (slave))
    Feedforward control (ratio)
    Put on process & instrumentation diagram (P&ID)
Control algorithm
    On/off
    PID (proportional-integral-derivative)
    Model based (MPC)
Implementation
    Computer + connect measurements (sensors) and valves (actuators)
Process engineer (YOU):
Responsible for items 1- 4
The most important is process understanding
 | Input 1 | input2
Output 1 | + | -
Output 2 | 0 | +
Process matrix
*(has some effect, but too small or with too much delay for control)
Avoid pairing on zero gain (otherwise you will depend on other loops being closed)
Also: Use for determining sign of controller gain (Kc)

## Slide 31: Example: Shower
 | Input 1 qc | Input2 qh
Output 1 T |  | 
Output 2 q |  | 
Define control objective (why control?)
    CVs: Control temperature T and flow q
Classify variables
    CVs (y): T, q
    MVs (u): qc (really zc), qh (really zh)
    Disturbances (d): Focus on main
Process description
    Flow sheet
    Model: Process matrix
Control structure
    Pairing of variables (Alt.1, Alt.2)
    Multivariable (Alt 3)
In this case the process matrix has no 0’s ) Interactive, so pairing is not obvious!
Multivariable control (“decoupling”) is used in practice:
One handle (up/down) for total flow (qh+qc), one (left/right) for ratio (qh/qc)
qc
qh
T
q
+
+ +
2021, 2024: Start lecture 4

## Slide 32: Decoupling shower using ARC
Comment:
Maybe better with FC on qC (upper left FC). Then need a subtraction qCs = (qC+qH)s- qH
ARC = Advanced Regulatory Control
Advanced regulatory control (for later)

## Slide 33: 3x3 pairing example
Inputs
Outputs
y1 + + +
y2 0 + -
y3 0 + 0
u1 u2 u3
Pairing: Choose one pairing from each row/column. Avoid pairing on 0’s

## Slide 34: Rules for pairing of variables and choice of control structure
The response (from input to output) should be fast, large and in one direction. Avoid pairing on 0! Avoid dead time and inverse responses!
The input (MV) should preferably affect only one output (to avoid interaction between the loops; want some 0’s in the process matrix)
Try to avoid input saturation (valve fully open or closed) in “basic” control loops for level and pressure
The measurement of the output y should be fast and accurate. It should be located close to the input (MV) and to important disturbances.
    Use extra measurements y2 and cascade control if this is not satisfied
The system should be simple
    Avoid too many feedforward and cascade loops
“Obvious” loops (for example, for level and pressure) should be closed first, before you spend too much time on deriving process matrices etc.
Main rule(1,2,4): “Pair close”

## Slide 35: Control hierarchy based on “time scale separation”
MPC or ARC (cascade/switching/…)
(slower advanced and multivariable control)
PID (fast “regulatory” control)
PROCESS
setpoints
setpoints
MPC = model predictive control
PID = proportional+integral+derivative control

## Slide 36: Example: Distillation
Here: Given feed (i.e., feedrate is disturbance)
Objective: “Stabilize” column + keep compositions in top and bottom constant
  But compositions measurements are delayed + unreliable
Classify variables
Process description
  Flowsheet
  Process matrix
Control structure: Stabilize column “profile” using sensitive temperature measurement.

## Slide 37
2024: This is at end of lecture 4
Material balances for condenser and reboiler:
dMD/dt = LD – L – D [mol/s]
dMB/dt = LB – V – B [mol/s]
Note: We could write balances on mass basis [kg/s], but for distillation mol/s is better because molar flowrates are almost constant inside the column (but not mass flowrates)
LD
LB
F = feed [mol/s]
D = distillate
B = bottoms
L = reflux
V = boilup = QB/
LD = condensate = QD/
QD [J/s] = cooling
QB [J/s] = heating
= heat of vaporization
(typical 40 kJ/mol]
Level H[m]:
Inventory M [mol] = V [m3] ρM [mol/m3]
Volume V = A H
Molar density c= ρ [kg/m3] / MW [kg/mol]
Data water:
ρ = 1000 kg/m3, MW = 18e-3 kg/mol, ρM=55e3 mol/m3

## Slide 38
CC
LV
Typical distillation control:
Level control using LV-configuration (reflux L and boilup V left for CC)
Two-point composition control (CC)
  with inner T-loop (cascade)
TC
Ts
xB
CC
xD
Slave (fast)
Master (slow)
2024: start lecture 5 (after finishing up example)

## Slide 39
XC
TC
FC
ys
y
Ls
Ts
L
T
z
XC
Cascade control
distillation
With slave flow controller +
slave T-controller in top
LC
LC

## Slide 40: Inventory control and TPM
Inventory control: Usually control of level and pressure
Throughput manipulator (TPM): Where the operator sets production rate
Usually TPM at feed, but better for economics: Close to production bottleneck
Radiation Rule for level and pressure control («to keep things flowing»): Inventory control should be radiating around TPM

## Slide 41: Rules for inventory control
Rule 1. Cannot control (set the flowrate) the same flow twice
Rule 2. Controlling inlet or outlet pressure indirectly sets the flow (indirectly makes it a TPM)
Rule 3. Follow the radiation rule whenever possible
Breaking the radiation rule leads to undesirable «long loops»*:
*A «Long loop» does not follow the «pair close» rule, and the functioning of a long loop depends on other loops being closed.
TPM
Comment: Originally the TPM was at the feed (F0) - but then the outflow (F3) reached saturation (so this became the TPM) – and we let F0 take over the inventory control in the last unit.
This may work OK if the inventory control in units 1 and 2 is very fast.
Unit 3
Unit 2
Unit 1

## Slide 42
QUIZ. Are these structures workable (consistent)? Yes or No?
TPM
TPM
TPM
TPM
Hint: What happens to the mass holdup inside the red box? Is it self-regulated?

## Slide 43
Quiz 2. Gas-liquid separator.
Where is TPM? Consistent (One is not)?
TPM
TPM
TPM
TPM:
control exit pessure
Case (a): Given feedrate. Could alternatively set p0
Cases (b) and (c): Gas production limiting
Case (d): Liquid production limiting
TPM
Doesn’t follow radiation rule +
Cannot have two TPMs
Rule: Setting in-pressure p0 sets inflow = TPM at inlet or inlet direction (no cases above)
Setting out-pressure pG sets outflow = TPM at outlet or outlket direction (offdiagonal two cases)
(a)
(d)
(b)
(c)