## Slide 1: Dynamics and PID control (part 2 of crash course)
Sigurd Skogestad
TexPoint fonts used in EMF.
Read the TexPoint manual before you delete this box.: AAAAAAAA

## Slide 2: Process dynamics
“Things take time”
Step response (response of output y to a step in input u):
  k = Δy(∞)/ Δu – process gain
   - process time constant (63%)
   - process time delay
Time constant : Sometimes equal to residence time = V[m3]/q[m3/s]
Dynamic model: Can find  (and k) from balance equations:
  Then rearrange to match standard form of 1st order linear differential equation:
Process
u
input
y

## Slide 3: Response of linear first-order system
Remember for first order response:
Starts increasing immediately
Would reach new steady state after time ¿ if it kepy going with the same slope
Reaches 63% of change after time ¿.
Approaches new steady state exponentially (has for practical purposes reached new steady state after about 4¿)
Δy(t=∞) = kΔu
Δu
Block diagram with transfer function
for first-order process
Δy

## Slide 4: More about valve equation
z
q [m3/s]
p1
p2
Linear valve: f(z)=z
Derivation: From Bernoulli’s equation for pressure drop (turbulent flow): Δpf = k ρ v2, v = q/A

## Slide 5: Even more about valve equation*
*From: S. Skogestad, Chemical and Energy Process Engineering, CRC Press, 2009

## Slide 6: Example dynamic model: Concentration change in mixing tank
  Assume constant V [m3]
  Assume constant density ρ [kg/m3]
  Assume, c (in tank) = c (outflow) [mol A/m3]
  Assume no reaction
  Balances:
  Mass
  Component:
c
V
inflow
outflow
 | Mass balance | Component balance
Inflow | ρqF [kg/s] | cF qF [mol A /s]
Outflow | ρq [kg/s] | c q [mol A/s]
Inventory (“state variable”) | ρV [kg] | c V [mol A]
q [m3/s]
qF [m3/s]
Inventory
cF
c

## Slide 7: Feedback control
Thermo-couple
D/A
(convert digital to analog signal)
A/D
(convert analog to digital signal)
Computer
(controller algorithm)
Hot water
T
Valve
Motor/
Amplifier/
Relay
Signal
[mV]
Signal
[mV]
[bar / psi/
Ampere]
Card in computer
Measument signal
[bits]
Setpoint, etc.
Input signal
[bits]
Card in computer
Control systems elements:
Sensor
Actuator

## Slide 8: Measurements
Pressure is usually the most robust, fast and cheap measurement
  So we use it also for
    Level (DP)
    Flow (DP for venturi or orifice)
Temperature is usually also robust and cheap
  Thermocouple, Thermistors (resistors), infrared, etc….
Composition is often difficult
  Gas chromotograph (GC) is best for low concentrations but it’s expensive and gives time delay (typical 5-10 minutes)

## Slide 9
e
ym
Block diagram of negative feedback control
Block diagram
C = Feedback Controller = ?
Process
gm

## Slide 10: Feedback controller
Controller
algorithm:
u = f(ys,ym)
Usually: u=f(e) where e=ys-ym
Measurement
ym
Setpoint
ys
Input (MV)
u
Simplest controller algorithm: On/off controller.
Example: Common thermostat in room
Works well for simple dynamics
Problem: Always cycles
Industry: Standard algorithm for SISO controllers: PID
Industry: Standard for interactive multivariable control: MPC (model predictive control)
y=T
u=Q (heat)

## Slide 11: How is ON/ON control for floor heating?
Exam Process control. Dec. 2024
Dynamic model:
Setpoint response for ON/OFF.
Start from T=0C and then step Setpoint to Ts=15C and after 5 hours to 20C
Conclusion: ON/OFF is Good for this application!!
General: Good for «simple» processes
File: on_off_control_exam2024.slx
T
Q
20h

## Slide 12: PID controller
Proportional control (P)
  Input change (u-u0) is proportional to control error e.
  Kc = proportional gain (tuning parameter)
  u0: = «bias»
Problems proportional control:
Get steady-state offset (especially if Kc is small)
Oscillates if Kc is too large (can get instability)
k = process gain = (steady-state)
Kc = controller gain
e

## Slide 13: P-control of typical process
Kc=1/k
Kc=2/k
Kc=4/k
Kc=8/k
ys (setpoint)
y
50% offset
20%
Initially at steady-state (y=ys=0). Change setpoint to ys=1 at t=1.
Process has time constant tau=1.5 min and delay theta=0.3min .
min

## Slide 14
Fix: Add Integral action (I)
Get PI-control:
¿I = integral time (tuning parameter)
e = ys – y (control error)
Note 1: Integral term will keep changing until e=0 ) No steady-state offset
Note 2: Small integral time gives more effect!
(so set ¿I = 99999 (large!) to turn off integral action)
Note 3: Integral action is also called «reset action» since it «resets» the bias.
Kc=2/k, τI=1.5 min
Process has theta=0.3 min and tau=1.5 min.
min

## Slide 15: Add also derivative action (D): Get PID controller
P-part: MV (Δu) proportional to error
    This is usually the main part of the controller!
I-part: Add contribution proportional to integrated error.
    Integral keeps changing as long as e≠0
    -> Will eventually make e=0 (no steady-state offset!)
Possible D-part: Add contribution proportional to change in (derivative of) error
    Can improve control for high-order (S-shaped process response) and unstable processes, but sensitive to measurement noise
I: Patient
P:Normal
D: Impatient

## Slide 16: Many alternative PID parameterizations
Also other:
  Proportional band = 100/Kc
  Reset rate = 1/ I
  Etc…..
NOTE: Always check the manual for your controller!
Comment 1: Often the D-action is not on the setpoint, so the D-term becomes - τD dy/dt
Comment 2: This is the «ideal» PID. In this course we also use the series PID (SIMC-rule). For PI they are the same.

## Slide 17: Digital implementation (practical in computer) of PID controller
Integral action = «Reset» of bias:

## Slide 18: PID controller tuning
Want the system to be (TRADE-OFF!)
Fast intitially (Kc large, D large)
Fast approach to steady state (I small)
Robust / stable (OPPOSITE: Kc small, I large)
Smooth use of inputs (OPPOSITE: Kc small, D small)

## Slide 19: Tuning of your PID controller I. “Trial & error” approach (online)
P-part: Increase controller gain (Kc) until the process starts oscillating or the input saturates
Decrease the gain (~ factor 2)
I-part: Reduce the integral time (I) until the process starts oscillating
Increase a bit (~ factor 2)
Possible D-part: Increase D and see if there is any improvement
Very common approach,
BUT: Time consuming and does not give good tunings: NOT recommended

## Slide 20: II. Model-based tuning (SIMC rule)
From step response obtain
  k = Δy(∞)/ Δu – process gain
   - process time delay
   - process time constant (63% after delay)
Proposed SIMC controller tunings
k = Δy(∞)/ Δu
Recommended approach

## Slide 21: Example SIMC rule
From step response
  k = Δy(∞)/ Δu = 10C / 1 kW = 10
   = 0.4 min (time constant)
   = 0.3 min (delay)
Proposed controller tunings

## Slide 22: Simulation PID control
Setpoint change at t=0 and input disturbance at t=5 min
  Well tuned (SIMC): Kc=0.07, taui=0.4min
  Too long integral time (Kc=0.07, taui=1 min) : settles slowly
  Too large gain (Kc=0.15, taui=0.4 min) – oscillates
  Too small integral time (Kc=0.07, taui=0.2 min) – oscillates
  Even more aggressive (Kc=0.12, taui=0.2 min) – unstable (not shown on figure)
2
1
3
4
1
2
3
4
Output (y)
Time [min]
setpoint
Comment: Can avoid the setpoint overshoot for curve 1 by adding derivative action (try taud=0.3/3=0.1 with series PID) but will be more sensitive to noise
Process has k=10, theta=0.3 min and tau=0.4 min.

## Slide 23: Comments tuning
Delay (θ) is feedback control’s worst enemy!
    Try to reduce it, if possible. Rule: ”Pair close”!
Common mistake: Wrong sign of controller!
  Controller gain (Kc) should be such that controller counteracts changes in output
  Need negative sign around the loop (”negative feedback”)
  Two ways of achieving this:
    (Most control courses:) Use a negative sign in the feedback loop. Then controller gain (Kc) should always have same sign as process gain (k)
    (Most real control systems*:) Always use Kc positive and select between
      ”Reverse acting” in the normal case when the process gain (k) is positive
        because MV (u) should go down when CV (y) goes up (to get negative feedback), for example, when we use heat (u=Q) to control room temperature (y=T).
      ”Direct acting” when k is negative
      Comment: This convention is common in process control (including Aspen/Hysys simulation software)
      BUT WARNING: Be careful and read manual! Some use «direct» and «reverse» opposite!, e.g., wikipedia on PID control:
      2021: https://en.wikipedia.org/wiki/PID_controller
* Including Emerson, Honeywell, ABB, Yokogawa.

## Slide 24
3. Integrating («slow») process: If the response is not settling after approximately 10 times the desired closed-loop time constant (so ¿/(¿c+θ) >4), then you can stop the experiment and approximate the response as an integrating process (with only two parameters, k’ and µ):
Δy
Δt
Integrating processes require mainly P-action and are difficult to control manually

## Slide 25
4. «Fast» process: If the response is fast compared to the desired closed-loop time constant (so ¿/(¿c+θ) < 0.25, approximately), then you dom’t really need so much P-action in the controller and you can approximate the response as a delay process (with only two parameters, k and µ):
Δy
Δt
Pure delay processes require mainly I-action and are easy to control manually
Gain, k=Δy/Δu
May use pure I-controller with KI=1/k(¿c+θ).
Same as PI with Kc=¿/k(¿c+θ) and ¿I =¿ for small ¿ (but then actual value of ¿ does not really matter).

## Slide 26
Example: Similar to shower process
u = Q
y = T
d = TF
Simulink model: tunepid1_ex1
Note: level control not explicitly included in simulation (assume constant level)
Looong pipe
µ=100s
¿=20s

## Slide 27: Disturbance response with no control
y = T
Looong pipe
µ=100s
¿=20s
Kc=0; taui=9999; % no control
%start simulation (press green button)
plot(time,u,time,T,time,Tf), axis([0 800 -1.5 1.5])
u = Q
u = Q
y = T
d = TF
d = TF

## Slide 28: P-control
u = Q
y = T
d = TF
TC
Ts
Offset
Kc=0.5; taui=9999; % P-control
%start simulation (press green button)
plot(time,u,time,T,time,Tf), axis([0 800 -1.5 1.5])

## Slide 29: SIMC PI control
u = Q
y = T
d = TF
TC
Ts
No offset
Kc=0.1; taui=20; % SIMC PI-control
%start simulation (press green button)
plot(time,u,time,T,time,Tf), axis([0 800 -1.5 1.5])

## Slide 30
Recommend: ¿c=delay µ=100s because it is more robust and gives no overshoot in u
y = T
u = Q
d = TF

## Slide 31
TC
T0s
TC
T0
Ts
Measure also T0: Cascade control is much better
Inner loop (T0): tauc=10
Outer loop (T): tauc=105
Slave controller
(inner loop)
Master controller
(outer loop)
Kc2=0.1;taui2=1; % inner loop with tauc2=10
Kc=0.119; taui=25; % outer loop with tauc=105
sim('tunepid1_ex1_cascade') %start simulation
plot(time,u,time,T,time,Tf,time,T0), axis([0 800 -1.5 1.5])
d = TF
y = T
u = Q

## Slide 32: Simulation: Room heater (2nd order dynamics ,NOT floor heating,)
Want to control y=T using electric heater. u=Q.
Heater: Min=0, Max=10 [kW]
Start: Cold room (0C).
Heat to setpoint=15 C and then to 20C
Dynamics:
  Heater, tau2=0.1 h (takes time to heat up metal of electric heater)
  Room, tau1=1h (residence time for air in room = m[kg]/w[kg/s])
  Delay, theta = 0.02 h = 1.2 min. (slow sensor for T)
  Resulting transfer function: G(s) = 3 e-0.02s / (s+1)(0.1s+1)
Consider: ON/OFF, P and PI
File: on_off_control0

## Slide 33: Simulation: Room heater (2nd order dynamics ,NOT floor heating,)
Want to control y=T using electric heater. u=Q.
Heater: Min=0, Max=10 [kW]
Start: Cold room (0C).
Heat to setpoint=15 C and then to 20C
Dynamics:
  Heater, tau2=0.1 h (takes time to heat up metal of electric heater)
  Room, tau1=1h (residence time for air in room = m[kg]/w[kg/s])
  Delay, theta = 0.02 h = 1.2 min. (slow sensor for T)
  Resulting transfer function: G(s) = 3 e-0.02s / (s+1)(0.1s+1)
Consider: ON/OFF, P and PI
File: on_off_control0

## Slide 34: On-Off control
y = temperature
r = setpoint y
u = heater (0-10)
Oscillates a little too much
  G(s) = 3 e-0.02s / (s+1)(0.1s+1)
h

## Slide 35: P control Kc=3
y = temperature
r = setpoint y
u = heater (0-10)
OFFSET (%) = 100%/(1+kKc)
=100/(1+3*3)=10%
  G(s) = 3 e-0.02s / (s+1)(0.1s+1)
h
h

## Slide 36: PI control Kc=2.5, tauI=0.56 (tauc=theta)
y = temperature
r = setpoint y
u = heater (0-10)
Oooops!
  G(s) = 3 e-0.02s / (s+1)(0.1s+1)
h

## Slide 37: PI control with anti-windup* Kc=2.5, tauI=0.56, tauT=tauI/2
y = temperature
r = setpoint y
u = heater (0-10)
THE BEST!
  G(s) = 3 e-0.02s / (s+1)(0.1s+1)
h
*Anti-windup stups integral action when input u saturates at umax=10 [kW]
(tauc=theta)

## Slide 38: Compare all
y = temperature
r = setpoint y
u = heater (0-10)
  G(s) = 3 e-0.02s / (s+1)(0.1s+1)
h
PI
P
ON/OFF
PI
PI w/ anti-windup
PI w/ anti-windup
P
ON/OFF

## Slide 39
File: on_off_control0

## Slide 40: Lab: The experimental setup
y=T
u=Q
This is the «Whistler»
y=T [C] (at top)
u=Q [0-1] (at bottom)
First we did a step response experiment where u was increased from 0 to 1 (manual vontrol). The temperature y=T increased from 20C to 54C (new steady state). This gives k=68. The dynamics are quite slow because it takes time to heat up the glass. , θ=5s, τ =120s
From this we obtained the model parameters and SIMC tunings (with τc=θ=5s)
We then put it into automatic and increased the setpoint to 70C. The input (u=Q) increased immediately to max=1, and we should then have stopped the integration («anit windup») but we had forgotten to do this and this is why you can see that u=Q stayed at max=1 even after y=T has passed the setpoint…. Not so good… but eventually we see that it was working well.
Note: Need to use «anti-windup» to avoid that the integral action in the controller keeps increasing u when it actually has saturated.

## Slide 41: The model. Step response: k=68, θ=5s, τ =120s The controller. SIMC (with τc=θ=5s): Kc=0.2, τI=40s

## Slide 42: The closed-loop response
y=T
ys=Ts =70C
u=Q
(The input is a bit noisy because of a noisy temperature measurement, but it works!)
max=1
min=0
Time (s)
Overshoots because of
WINDUP problem