Control Structure Analysis for an Activated Sludge Process

Michela Mulas(1), Sigurd Skogestad(2)

(1) Dipartimento di Ingegneria Chimica e Materiali, Università di Cagliari, Italy

(2) Department of Chemical Engineering, NTNU, Trondheim, Norway

Following the plantwide control structure design procedure proposed by Skogestad (2004), in this paper we find candidate controlled variables with good self-optimizing properties for an activated sludge process. In particular, as a case study the TecnoCasic wastewater treatment plant, located near Cagliari (Italy) is considered.

# 1. Introduction

In the last decades, urban population growth and industrial expansion have increased the amount and diversity of wastewaters generated. The increasing public awareness is reflected in more stringent regulations and has considerably increased the requirements imposed on a Wastewater Treatment Plant (WWTP), which has gained a more and more important role in water resource prevention. Furthermore, in some countries the wastewater treatment has become part of a production process, essentially for fresh water reuse purpose; consequently quality control of the effluent will be very important since failure of the treatment process may lead to significant production losses. This situation demands more efficient procedures for WWTP management and control.

Inside the plant, the Activated Sludge Process (ASP) is the most extensively used wastewater technology for biological treatment of liquid wastes. One way to improve the system behaviour is to introduce an advanced control structure but, from a control engineer’s point of view, the ASP is a complex topic for several reasons. First of all, it is a biological process where temperature, composition of the influent water, amount of biomass and flows vary with time. Furthermore the process is nonlinear and has stiff dynamics with time constants ranging from seconds to months. Due to this issue, it might be a difficult task to evaluate different kinds of process control strategies objectively. Following the control structure design proposed by Skogestad (2004), this paper proposes how to implement the optimal operation policy for an ASP.

# 2. Activated Sludge Process – Models and Simulation

Traditionally, ASP involves an anoxic zone followed by an aerobic zone, in order to obtain a nitrification and denitrification processes, a settler from which the major part of the biomass is recycled into the anoxic basin follows (Figure 1).

Figure 1 Simplified representation of an Activated Sludge Process

To represent the whole system, two reference models were chosen: the Activated Sludge Model No. 1 (ASM1), proposed by the International Association on Water Pollution Research and Control (Henze et al., 1987), was chosen as the biological process model, and the double-exponential settling velocity function of Takács et al. (1991) was chosen as a representation of the settling process.

The ASM1 provides a detailed description of biochemical processes including carbon oxidation and nitrogen removal; including 13 state variables. The resulting model is nonlinear, with reaction rate Monod-like, it presents high interdependence of the state variables, lacking identifiability and verifiability (Jeppsson, 1996). The kinetic and stoichiometric model parameters are to be defined in order to calibrate the model.

The settler is divided in ten layers of constant thickness. The model is based on the solid flux concept: a mass balance is performed around each layer, providing the simulation of the solids profile throughout the settling column under both steady state and dynamic conditions.

As an example, we consider the TecnoCasic wastewater treatment plant located near Cagliari (Italy). The liquid waste collected derives from municipalities (30%) and industries (70%). The removal of nitrogen and organic matter is obtained with a continuous activated sludge process. In the reactor a pre-denitrification is obtained followed by a nitrification, supplying a low airflow, needed just for mixing purposes, in the fist half basin and a higher air flow in the last half. The aeration is obtained with fine bubbles supplied air diffusers, located in the bottom. The average of two oxygen sensors signals located in the anoxic and aerobic zone is compared with a constant DO setpoint of 2.5 gO2/m. The controller maintains the desired oxygen setpoint by manipulating of the aeration supply. The TecnoCasic activated sludge configuration is the same showed in Figure 1: from the secondary settler, the sludge is partially recirculated to the reactor (returned activated sludge, RAS) and partially wasted as excess sludge (waste activated sludge, WAS). The global process is considered isothermal (around 20 °C).

A representation of the TecnoCasic plant can be implemented in different ways, using different software and simulators. In this work we choose to do it in Matlab (Version 6.5) language. Data provided by the real plant were the following: flow rates, dissolved oxygen concentration in the basin measured on-line, daily COD and nitrogen (nitrite, nitrate, TKN, ammonia) concentration in inflow and outflow streams available every two or three days. COD and nitrogen measurements were obtained off-line in the TecnoCasic laboratory. These data allowed calibrating the model, namely the parameter values and an initialization procedure for the states are specified, using the Matlab Optimization toolbox and a process insight the models, for both bioreactor and secondary settler.

# 3. A “Top-Down” Control Analysis

Following the plantwide control structure design procedure proposed by Skogestad (2004), we find candidate controlled variables with good self-optimizing properties for an activated sludge process. The central issue when searching for the self-optimizing control structure is to decide how to best implement the optimal policy in presence of uncertainty. Selecting the right set of controlled variables to be kept at constant setpoints allows this.

Step 1: Identify operational constraints, and a scalar cost function J to be minimized.

## Cost Function

The optimizing control problem can be formulated as:

minJ(x,u,d)

subjected to: f(x,u,d)=0; g(x,u,d)≤0.

Where f is the process model, g are the inequality constraints, x are the state variables, u are the independent variables we can affect (degree of freedom for optimization), and d are independent variables we can not affect (disturbances). The overall costs in wastewater treatment are highly depending on the wastewater treatment system. In our work we have considered essentially the energy consumption in terms of aeration power, because this highly depends on plant operation and because this represents the major economic duty in our ASP. Energy costs for aeration will typically be 50% to 90% of all energy consumed at a wastewater treatment plant. For that reason, the cost function is the aeration power in the aeration tank, and the operational cost function J to be minimized is:

J=Qair=(QairDeNitr+QairNitr)

Operational Constraints

As operational constraints we can identify those related to the flow in the tank, to the aeration compressor, to the valve in the plant, etc. But as most important, we can identify the DO concentrations in the aerated tank (either in the denitrification or nitrification zone), and the constraint for a well operating behaviour of the secondary settler.

Dissolved Oxygen (DO) concentration is one of the principal parameters in an ASP. In the aerobic part of an ASP the DO concentration should be sufficient to supply enough oxygen to the microorganisms in the sludge: 2 gO2/m3 is a commonly used value. Values above 4 gO2/m3 do not improve operation significantly, but increased the aeration cost considerably (Metcalf & Eddy, 1991). In the anoxic zone, a lower aeration is needed in order to satisfy only the mixing requirement in the denitrification zone. Summarizing, we have the following DO constraints:

- DO concentration in the anoxic zone: 0.05 gO2/m3 DO 0.5 gO2/m3;

- DO concentration in the aerobic zone: 1.5 gO2/m3 DO 4 gO2/m3.

Considering the TecnoCasic plat, due to the aeration control loop adopted, the actual DO concentration in the nitrification zone is almost always greater than 4 gO2/m3. During the steady state simulation we reduced the actual value of the DO in the aerobic zone to 3 gO2/m3, whereas in the anoxic zone the DO concentration is equal to 0.1 gO2/m3.

We know that the excess activated sludge produced each day must be wasted to maintain a given food-to-microorganisms ratio (F/M) or mean cell-residence time (also known as sludge residence time, SRT, or sludge age). Typical values for the F/M reported in literature vary from 0.05 to 1.0 [gCOD gSS-1 d-1]. On the basis of laboratory studies and actual operating data, it has been found that SRT of about 3 to 15 days results in the production of a stable, high quality effluent and a sludge with excellent settling characteristics (Metcalf & Eddy, 1991).  If the SRT constraint is satisfied also the F/M ratio does. So, we find one of those as a constraint for the sludge quality.

Effluent Constraints

The main aim of a wastewater treatment plant is to maintain satisfactory concentrations of organics, nitrogen, phosphorus and other pollutant. For that, the final constraint of our ASP is defined by the legislation requirement for an effluent deriving from a wastewater treatment plant. Hence, the overall behaviour of the process has to be subjected to these constraints: COD  125 gCOD/m3, TSS (Total Suspended Solids)  35 gSS/m3 and TN (Total Nitrogen)  18 gN/m3.

Disturbances

Typically influent characteristics, flowrates and nutrient loading and in some plants temperature, vary by a factors of two to ten (Olsson and Newell, 2001). In the TecnoCasic plant an equalization tank is present at the top of the activated sludge process. For that reason in our case the only disturbances that we must take into account are the influent compositions, which we cannot affect. The influent flow rate can be considered constant if we consider that some measurement noise can be present. Hence the following disturbances have been considered: d1 = COD  30%, d2 =TKN  30%, d3=Ammonia  30%.

Step 2. Manipulated variables and degree of freedom

First of all, we have to identify the number of degree of freedom for control, Nm, this is usually obtained from process insight as the number of independent variables that can be manipulated by external means (which in process control is the number of adjustable valves plus the number of other adjustable electrical and mechanical variables). Next, we must identify the Nopt, the optimization degree of freedom that affect the operational cost J.

For the TecnoCasic Plant, we have: Nm is equal to 7, if we include the influent flow rate. Namely, the output flow from the aeration tank should be not taken into account since it is actually self-regulating; the same can be said about the effluent flow from the secondary settler. Therefore, we have Nm=5. The optimization is generally subject to several constraints and the Nopt degrees of freedom should be used to satisfy the constraints and optimize the operation. In our case we have Nopt=3, because we are not considering the RAS and the influent flowrate. Usually, the RAS flow is proportional to the influent flow, which can be considered constant (an equalisation tank is present in the plant).  For that reason the RAS flow has been considered constant and without influence at the steady state behaviour.  The number of “free” (unconstrained) degree of freedom than are left to optimize the airflow rate in our activated sludge process is

Nopt,free=Nopt−Nactive

where Nactive is the number of active constraints. If we consider as active constraints only the DO concentrations in both anoxic an aerated zone, we found Nopt,free=1.

Step 3. Optimization

In particular, we are interested in a steady state optimization of the activated sludge process in the TecnoCasic plant. For the particular configuration of the plant in study, we consider as an “optimum” the values obtained with the 15 days averaged data of the influent composition and flow, and we calculate our “optimal” operation costs as Jopt=29926 m3/d. The actual operation cost will depend on the control strategy used to adjust the WAS flowrate during operation.

Step 4. Primary Controlled Variables

We have showed that the system has 1 degree of freedom during operation. How should the degree of freedom be set? Which variable should be kept constant? To identify good candidate controlled variables, c, one should look for variables that satisfy all of the following requirements (Skogestad, 2000):

- The optimal value of c should be insensitive to disturbance,

- The controlled variable should be easy to measure and control;

- The value of c should be sensitive to changes in the manipulated variables (the steady degree of freedom).

The following candidates for the controlled variable c are suggested:

| c1 = SRT | c2 = F/M | c3 = TNDeNitr | c4 = WAS |
| --- | --- | --- | --- |

The first three are closed loop policies, whereas the last one is an open loop strategy. The controlled variables c1 and c2 are a combination of measured variables. A proper SRT calculation involves the estimation of the average total sludge content as well as the average total sludge withdrawal. The control of the F/M ratio involves the measurements of the influent “food” concentration and the suspended solids in the bioreactor. The c3 controlled variable is the Total Nitrogen concentration in the anoxic zone. It is a composite ASM1 variable and comprises particulate and soluble state variables. The last control strategy that we analyze is the open loop one. This is a poor policy to adopt, but is frequently used and is a good kind of reference to understand how the system could operate if there is any control applied. In Table 1 only the results for the cost function are reported. As we can note, the configuration that present a better response is the c3 controlled variable. This is because the anoxic zone behaviour can influence the overall cost function (even if the air flowrate in it is quite small compared with the aerobic part).

|  |  | Positive Deviations | Negative Deviations |  | Positive Deviations |  |  | Negative Deviations |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| c1 = SRT Closed Loop |  |  |  |  |  | c3 = TNDeNitr Closed Loop |  |  |
| d1 | 38682 |  |  | 24800 | 38679 |  | 24816 |  |
| d2 | 33756 |  |  | 27006 | 33765 |  | 26967 |  |
| d3 | 34182 |  |  | 29607 | 30252 |  | 29591 |  |
| c2 = F/M Closed Loop |  |  |  |  |  | c4 = Open Loop |  |  |
| d1 | 38628 |  |  | 24589 | 38650 |  | 24758 |  |
| d2 | 33648 |  |  | 26968 | 33749 |  | 26991 |  |
| d3 | 30255 |  |  | 29594 | 34171 |  | 29607 |  |

Table1 Cost function as a function of influent disturbances

# 4. Conclusions

In this work, we have considered alternative controlled variables for the TecnoCasic activated sludge process. The goal of this work has not been to find an optimal operating point for an activated sludge process. The main idea is to find a set of candidate controlled variables with good self-optimizing properties. Following the plantwide control structure design procedure proposed by Skogestad (2004), we have found that a better response to influent disturbances can be obtained using as controlled variable the total Nitrogen in the anoxic zone, manipulating the WAS flowrate.

# 5. References

Henze, M., Leslie Grady C. P., Gujer W., Maris G. V. R., and Matsuo T., 1987, Activated Sludge Model No. 1, I.A.W.Q. Sci. and Tech. Report No. 1, London, U.K.

Jeppsson, U., 1996, Modelling Aspects of Wastewater Treatment Processes. Ph.D. dissertation, IEA, Lund Institute of Technology, Lund, Sweden.

Metcalf & Eddy Inc., 1991, Wastewater Engineering, Treatment, disposal, reuse, McGraw Hill.

Olsson G., Newell B., 2001, Wastewater treatment systems. Modelling, Diagnosis and Control, IWA Publishing.

Skogestad, S., 2000, Plantwide control: the search for the self-optimizing control structure, Journal of Process Control, 10, 487-507.

Skogestad, S., 2004, Control structure design for complete chemical plants, Comp. Chem. Eng. 28, 219-234.

Takács I., Patry G. G., Nolasco D., 1991, A dynamic model of the clarification-thickening process, Wat. Res., Vol. 25, No. 10, 1263-1271.

The phosphorus nutrient is not considered due to the lower urban waste, it is only present as a manual dosage, in order to respect the nutrient ratio: COD(Chemical Oxygen Demand):N:P=100:5:1, (Metcalf & Eddy, 1991).