## Slide 1: Economic process control Introduction
Sigurd Skogestad, NTNU
Nitin Kaitsha, IIT Kanpur

## Slide 2: Shortcourse PSE Asia 2019: Economic process control 13 January 2019 from 9:00-17:00 at Faculty of Engineering, Chulalongkorn University
Presenters:
Professor Sigurd Skogestad, NTNU
Professor Nitin Kaistha, IIT Kanpur (case studies)
This workshop focuses on the big picture when designing a control system for process plants. The overall objectives is to maximize the operational profit. This should also be the basis for designing the control system, all the way from PID controllers at the bottom of the control hierarchy to the possible RTO layer at the top.
09.00 Session 1. Overview of economic plantwide control
- Control degrees of freedom
- Our paradigm: Hierarchical decision (control) layer
- What is optimal operation?
- Distillation examples
10.15 Coffee break
10.30 Session 2. What to control? (Selection of primary controlled variables based on economics)
- Degrees of freedom
- Optimization
- Active constraints
- Self-optimizing control
11.30 Session 3. Where to set the production rate and bottleneck
- Inventory control
- Consistency
- Radiation rule
- Location of throughput manipulator (TPM)
12.00 Lunch
13.00 Session 4. Design of the regulatory control layer ("what more should we control")
- PID control, Stabilization
- Secondary controlled variables (measurements)
- Pairing with inputs
14.00 Case studies (1415: Coffee break)
15.00 Session 5 Design of supervisory control layer
- Cascade control
- Switching between active constraints
- MV saturation (SIMO controllers) : Split range control / Controllers with different setpoints
- CV changes: Selectors
- Decentralized versus centralized (MPC)
Session 6. Real-time optimization (see plenary tomorrow)
Alternative implementations:
- Conventional RTO
- Dynamic RTO / Economic MPC
- Combination with Self-optimizing control
- Extremum seeking control / NCO tracking / Hill climbing
16.00 Session 7 Case studies (throughout the day)

## Slide 3: Part 1. Plantwide control
Introduction to plantwide control (what should we really control?)
Introduction.
  Objective: Put controllers on flow sheet (make P&ID)
  Two main objectives for control: Longer-term economics (CV1) and shorter-term stability (CV2)
  Regulatory (basic) and supervisory (advanced) control layer
Optimal operation (economics)
  Define cost J and constraints
  Active constraints (as a function of disturbances)
  Selection of economic controlled variables (CV1). Self-optimizing variables.

## Slide 4: Sigurd Skogestad
1955: Born in Flekkefjord, Norway
1978: MS (Siv.ing.) in chemical engineering at NTNU
1979-1983: Worked at Norsk Hydro co. (process simulation)
1987: PhD from Caltech (supervisor: Manfred Morari)
1987-present: Professor of chemical engineering at NTNU
1999-2009: Head of Department
2015-..: Director SUBPRO (Subsea research center at NTNU)
Book: Multivariable Feedback Control (Wiley 1996; 2005)
  1989: Ted Peterson Best Paper Award by the CAST division of AIChE
  1990: George S. Axelby Outstanding Paper Award by the Control System Society of IEEE
  1992: O. Hugo Schuck Best Paper Award by the American Automatic Control Council
  2006: Best paper award for paper published in 2004 in Computers and chemical engineering.
  2011: Process Automation Hall of Fame (US)
  2012: Fellow of American Institute of Chemical Engineers (AIChE)
  2014: Fellow of International Federation of Automatic Control (IFAC)

## Slide 5: Nitin Kaistha
Professor at IIT Kanpur

## Slide 6: Trondheim, Norway

## Slide 7
Trondheim
Oslo
UK
NORWAY
DENMARK
GERMANY
North Sea
SWEDEN
Arctic circle

## Slide 8
NTNU,
Trondheim

## Slide 9: Why control?
Operation
time
Actual value(dynamic)
Steady-state (average)
In practice never steady-state:
  Feed changes
  Startup
  Operator changes
  Failures
  …..
Control is needed to reduce the effect of disturbances
30% of investment costs are typically for instrumentation and control
“Disturbances” (d’s)

## Slide 10: Countermeasures to disturbances (I)
Eliminate/Reduce the disturbance
  Design process so it is insensitive to disturbances
      Example: Use buffertank to dampen disturbances
  Detect and remove source of disturbances
      “Statistical process control”
      Example: Detect and eliminate variations in feed composition
inflow
outflow
∞
Tin
Tout

## Slide 11: Countermeasures to disturbances (II)
II. Process control
Do something (usually manipulate valve)
to counteract the effect of the disturbances
  (a) Manual control: Need operator
  (b) Automatic control: Need measurement + automatic valve + computer
    Goals automatic control:
      Smaller variations
        more consistent quality
        More optimal
      Smaller losses (environment)
      Lower costs
      More production
    Industry: Still large potential for improvements!

## Slide 12: Classification of variables
Process
u
input (MV)
y
output (CV)
d
Independent variables (“the cause”):
  Inputs (MV, u): Variables we can adjust (valves)
  Disturbances (DV, d): Variables outside our control
Dependent (output) variables (“the effect or result”):
  (c) Primary outputs (CVs, y1): Variables we want to keep at a given setpoint
  (d) Secondary outputs (y2): Extra measurements that we may use to improve control

## Slide 13: Inputs for control (MVs)
Usually: Inputs (MVs) are valves.
  Physical input is valve position (z), but we often simplify and say that flow (q) is input
Valve Equation

## Slide 14: Notation feedback controllers (P&ID)
TC
2nd letter:
C: controller
I: indicator (measurement)
T: transmitter (measurement)
1st letter: Controlled variable (CV) = What we are trying to control (keep constant)
T: temperature
F: flow
L: level
P: pressure
DP: differential pressure (Δp)
A: Analyzer (composition)
C: composition
X: quality (composition)
H: enthalpy/energy
Ts
(setpoint CV)
T
(measured CV)
MV (could be valve)

## Slide 15
LC
H
Hs
Inflow (d)
Outflow (u)
INPUT (u): OUTFLOW (Input for control!)
OUTPUT (y): LEVEL
DISTURBANCE (d): INFLOW
Example: Level control
CLASSIFICATION OF VARIABLES:

## Slide 16: How we design a control system for a complete chemical plant?
Where do we start?
What should we control? and why?
etc.
etc.

## Slide 17: Plantwide control = Control structure design
Not the tuning and behavior of each control loop,
But rather the control philosophy of the overall plant with emphasis on the structural decisions:
  Selection of controlled variables (“outputs”)
  Selection of manipulated variables (“inputs”)
  Selection of (extra) measurements
  Selection of control configuration (structure of overall controller that interconnects the controlled, manipulated and measured variables)
  Selection of controller type (LQG, H-infinity, PID, decoupler, MPC etc.).
That is: Control structure design includes all the decisions we need make to get from ``PID control’’ to “PhD” control

## Slide 18: Previous work on plantwide control:
Page Buckley (1964) - Chapter on “Overall process control” (still industrial practice)
Greg Shinskey (1967) – process control systems
Alan Foss (1973) - control system structure
Bill Luyben et al. (1975- ) – case studies ; “snowball effect”
George Stephanopoulos and Manfred Morari (1980) – synthesis of control structures for chemical processes
Ruel Shinnar (1981- ) - “dominant variables”
Jim Downs (1991) - Tennessee Eastman challenge problem
Larsson and Skogestad (2000): Review of plantwide control

## Slide 19
Alan Foss (“Critique of chemical process control theory”, AIChE Journal,1973):
The central issue to be resolved ... is the determination of control system structure. Which variables should be measured, which inputs should be manipulated and which links should be made between the two sets? There is more than a suspicion that the work of a genius is needed here, for without it the control configuration problem will likely remain in a primitive, hazily stated and wholly unmanageable form. The gap is present indeed, but contrary to the views of many, it is the theoretician who must close it.

## Slide 20: Main objectives control system
Economics: Implementation of acceptable (near-optimal) operation
Regulation: Stable operation
ARE THESE OBJECTIVES CONFLICTING?
Usually NOT
  Different time scales
    Stabilization fast time scale
  Stabilization doesn’t “use up” any degrees of freedom
    Reference value (setpoint) available for layer above
    But it “uses up” part of the time window (frequency range)

## Slide 21: Optimal operation (economics)
Example of systems we want to operate optimally
Process plant
  minimize J=economic cost
Runner
  minimize J=time
«Green» process plant
  Minimize J=environmental impact (with given economic cost)
General multiobjective:
  Min J (scalar cost, often $)
  Subject to satisfying constraints (environment, resources)

## Slide 22
Theory: Optimal operation
Objectives
Present state
Model of system
Theory:
  Model of overall system
  Estimate present state
  Optimize all degrees of freedom
Problems:
  Model not available
  Optimization complex
  Not robust (difficult to handle uncertainty)
  Slow response time
Process control:
  Excellent candidate for centralized control
(Physical) Degrees of freedom
CENTRALIZED
OPTIMIZER

## Slide 23: Practice: Engineering systems
Most (all?) large-scale engineering systems are controlled using hierarchies of quite simple controllers
  Large-scale chemical plant (refinery)
  Commercial aircraft
100’s of loops
Simple components:
  on-off + PI-control + nonlinear fixes + some feedforward
Same in biological systems

## Slide 24
Practical operation: Hierarchical structure
Manager
Process engineer
Operator/RTO
Operator/”Advanced control”/MPC
PID-control
u = valves
Our Paradigm

## Slide 25
Practice: Process operation
Practice:
Hierarchical structure
Each layer has its own goal (”default action”):
  Keep CV at given setpoint
Boss: layer above (adjusts setpoint)
Goal each layer: Action without boss is «Self-optimizing»
CV = controlled variable

## Slide 26
cs = y1s
MPC
PID
y2s
RTO
Follow path (+ look after other variables)
Stabilize + avoid drift
Min J (economics)
u (valves)
OBJECTIVE
Dealing with complexity
Plantwide control: Objectives
The controlled variables (CVs)
interconnect the layers
Notes: 26

## Slide 27: Translate optimal operation into simple control objectives: What should we control?
CV1 = c ? (economics)
CV2 = ? (stabilization)

## Slide 28: CV1 = Economic controlled variables
Systematic procedure for selecting economic controlled variables (CV1)
  Active constraints
  Remaining unconstrained degrees of freedom:
    «Self-optimizing» variables

## Slide 29: Outline
Skogestad procedure for control structure design
  I Top Down
    Step S1: Define operational objective (cost) and constraints
    Step S2: Identify degrees of freedom and optimize operation for disturbances
    Step S3: Implementation of optimal operation
      What to control ? (CV1) (active constraints, self-optimizing variables)
    Step S4: Where set the production rate? (Inventory control)
  II Bottom Up
    Step S5: Regulatory control: What more to control to stabilize (CV2) ?
    Step S6: Supervisory control: Control CV1 and keep feaiable oparationm
    Step S7: Real-time optimization

## Slide 30: Step S1. Define optimal operation (economics)
What are we going to use our degrees of freedom (u=MVs) for?
Typical cost function*:
*No need to include fixed costs (capital costs, operators, maintainance) at ”our” time scale (hours)
Note: J=-P where P= Operational profit
J = cost feed + cost energy – value products

## Slide 31: Optimal operation distillation column
Distillation at steady state with given p and F: N=2 DOFs, e.g. L and V (u)
Cost to be minimized (economics)
  J = - P where P= pD D + pB B – pF F – pVV
Constraints
  Purity D: For example xD, impurity < max
  Purity B: For example, xB, impurity < max
  Flow constraints: min < D, B, L etc. < max
  Column capacity (flooding): V < Vmax, etc.
  Pressure: p has given setpoint (can be given up, but need pmin < p < pmax)
  Feed: F has given setpoint (can be given up)
Optimal operation: Minimize J with respect to steady-state DOFs (u)
value products
cost energy (heating+ cooling)
cost feed

## Slide 32: Step S2. Optimize (a) Identify degrees of freedom (b) Optimize for expected disturbances
Need good model, usually steady-state
Optimization is time consuming! But it is offline
Main goal: Identify ACTIVE CONSTRAINTS
A good engineer can often guess the active constraints

## Slide 33: Step S2a: Degrees of freedom (DOFs) for operation
NOT as simple as one may think!
To find all operational (dynamic) degrees of freedom:
Count valves! (Nvalves)
“Valves” also includes adjustable compressor power, etc.
Anything we can manipulate!
BUT: not all these have a (steady-state) effect on the economics
Steady-state DOFs

## Slide 34: Steady-state degrees of freedom (DOFs)
IMPORTANT!
DETERMINES THE NUMBER OF VARIABLES TO CONTROL!
No. of primary CVs = No. of steady-state DOFs
CV = controlled variable
Methods to obtain no. of steady-state degrees of freedom (Nss):
Equation-counting
  Nss = no. of variables – no. of equations/specifications
  Very difficult in practice
Valve-counting (easier!)
  Nss = Nvalves – N0ss – Nspecs
  Nvalves: include also variable speed for compressor/pump/turbine
  Nspecs: Equality constraints (normally included in constraints)
  N0ss = variables with no steady-state effect
    Inputs/MVs with no steady-state effect (e.g. extra bypass)
    Outputs/CVs with no steady-state effect that need to be controlled (e.g., liquid levels)
Potential number for some units (useful for checking!)
Correct answer: Will eventually find it when we perform optimization
Steady-state DOFs

## Slide 35: Does a pump give a degree of freedom?
Yes, if it has variable speed drive

## Slide 36
Nvalves = 6 , N0y = 2* ,
NDOF,SS = 6 -2 = 4 (including feed and pressure as DOFs)
Typical Distillation column
*N0y : no. controlled variables (liquid levels) with no steady-state effect
4 DOFs:
With given feed and pressure:
NEED TO IDENTIFY 2 more CV’s
- Typical: Top and btm composition
1
2
3
4
5
6
Steady-state DOFs

## Slide 37: Steady-state degrees of freedom (Nss): 3. Potential number for some process units
each external feedstream: 1 (feedrate)
splitter: n-1 (split fractions) where n is the number of exit streams
mixer: 0
compressor, turbine, pump: 1 (work/speed) (BUT: Must have variable speed)
adiabatic flash tank: 0*
liquid phase reactor: 1 (holdup reactant)
gas phase reactor: 0*
heat exchanger: 1 (bypass or flow of cooling/heating)
column (e.g. distillation) excluding heat exchangers: 0* + no. of sidestreams
pressure* : add 1DOF at each extra place you set pressure (using an extra valve, compressor or pump), e.g. in adiabatic flash tank, gas phase reactor or absorption column
*Pressure is normally assumed to be given by the surrounding process and is then not a degree of freedom
Ref: Araujo, Govatsmark and Skogestad (2007)
Extension to closed cycles: Jensen and Skogestad (2009)
Real number may be less, for example, if there is no bypass valve or no variable speed
Steady-state DOFs

## Slide 38
“Potential number”,
Nss= 0 (column distillation) + 1 (feed) + 2*1 (heat exchangers) + 1 (split) = 4
With given feed and pressure: N’ss = 4 – 2 = 2
Distillation column (with feed and pressure as DOFs)
split
Steady-state DOFs

## Slide 39: Step S2b: Optimize for expected disturbances
What are the optimal values for our degrees of freedom u (MVs)?
Minimize J with respect to u for given disturbance d (usually steady-state):
  minu J(u,x,d)
  subject to:
  Model equations (e,g, Hysys): f(u,x,d) = 0
  Operational constraints: g(u,x,d) < 0
  OFTEN VERY TIME CONSUMING
  Commercial simulators (Aspen, Unisim/Hysys) are set up in “design mode” and often work poorly in “operation (rating) mode”.
  Optimization methods in commercial simulators often poor
    We use Matlab or even Excel “on top”
J = cost feed + cost energy – value products

## Slide 40: Step S3: Implementation of optimal operation
Have found the optimal way of operation. How should it be implemented?
What to control ? (primary CV’s).
  Active constraints
  Self-optimizing variables (for unconstrained degrees of freedom)
Objective: Move optimization into control layer

## Slide 41: Optimal operation of runner
  Cost to be minimized, J=T
  One degree of freedom (u=power)
  What should we control?
Optimal operation - Runner

## Slide 42: 1. Optimal operation of Sprinter
  100m. J=T
  Active constraint control:
    Maximum speed (”no thinking required”)
    CV = power (at max)
Optimal operation - Runner

## Slide 43: 2. Optimal operation of Marathon runner
    40 km. J=T
    What should we control? CV=?
    Unconstrained optimum
Optimal operation - Runner
u=power
J=T
uopt

## Slide 44
Any self-optimizing variable (to control at constant setpoint)?
    c1 = distance to leader of race
    c2 = speed
    c3 = heart rate
    c4 = level of lactate in muscles
Optimal operation - Runner
Self-optimizing control: Marathon (40 km)

## Slide 45: Conclusion Marathon runner
c = heart rate
select one measurement
CV = heart rate is good “self-optimizing” variable
Simple and robust implementation
Disturbances are indirectly handled by keeping a constant heart rate
May have infrequent adjustment of setpoint (cs)
Optimal operation - Runner
c=heart rate
J=T
copt

## Slide 46: Step 3. What should we control (c)? (primary controlled variables y1=c)
Selection of controlled variables c
  Control active constraints!
  Unconstrained variables: Control self-optimizing variables!

## Slide 47: Expected active constraints distillation
Both products (D,B) generally have purity specs
Valuable product: Purity spec. always active
  Reason: Amount of valuable product (D or B) should always be maximized
    Avoid product “give-away” (“Sell water as methanol”)
    Also saves energy
Control implications:
ALWAYS Control valuable product at spec. (active constraint).
May overpurify (not control) cheap product
valuable
product
methanol
+ max. 0.5%
water
cheap product
(byproduct)
water
+ max. 2%
methanol
methanol
+ water
Selection of CV1

## Slide 48: Example with Quiz: Optimal operation of two distillation columns in series

## Slide 49: Operation of Distillation columns in series With given F (disturbance): 4 steady-state DOFs (e.g., L and V in each column)
DOF = Degree Of Freedom
Ref.: M.G. Jacobsen and S. Skogestad (2011)
Energy price: pV=0-0.2 $/mol (varies)
Cost (J) = - Profit = pF F + pV(V1+V2) – pD1D1 – pD2D2 – pB2B2
> 95% B
pD2=2 $/mol
F ~ 1.2mol/s
pF=1 $/mol
< 4 mol/s
< 2.4 mol/s
> 95% C
pB2=1 $/mol
N=41
αAB=1.33
N=41
αBC=1.5
> 95% A
pD1=1 $/mol
QUIZ: What are the expected active constraints?
1. Always. 2. For low energy prices.
QUIZ 1

## Slide 50: Operation of Distillation columns in series With given F (disturbance): 4 steady-state DOFs (e.g., L and V in each column)
DOF = Degree Of Freedom
Ref.: M.G. Jacobsen and S. Skogestad (2011)
Energy price: pV=0-0.2 $/mol (varies)
Cost (J) = - Profit = pF F + pV(V1+V2) – pD1D1 – pD2D2 – pB2B2
> 95% B
pD2=2 $/mol
F ~ 1.2mol/s
pF=1 $/mol
< 4 mol/s
< 2.4 mol/s
> 95% C
pB2=1 $/mol
1. xB = 95% B
Spec. valuable product (B): Always active!
Why? “Avoid product give-away”
N=41
αAB=1.33
N=41
αBC=1.5
> 95% A
pD1=1 $/mol
2. Cheap energy: V1=4 mol/s, V2=2.4 mol/s
Max. column capacity constraints active!
Why? Overpurify A & C to recover more B
QUIZ: What are the expected active constraints?
1. Always. 2. For low energy prices.
Hm….?
SOLUTION QUIZ 1

## Slide 51: Control of Distillation columns in series
Given
LC
LC
LC
LC
PC
PC
QUIZ. Assume low energy prices (pV=0.01 $/mol).
How should we control the columns?
HINT: CONTROL ACTIVE CONSTRAINTS
Red: Basic regulatory loops
QUIZ 2

## Slide 52: Control of Distillation columns in series
Given
LC
LC
LC
LC
PC
PC
Red: Basic regulatory loops
CC
xB
xBS=95%
MAX V1
MAX V2
1 unconstrained DOF (L1):
Use for what?? CV=?
Not: CV= xA in D1! (why? xA should vary with F!)
Maybe: constant L1? (CV=L1)
Better: CV= xA in B1? Self-optimizing?
General for remaining unconstrained DOFs:
LOOK FOR “SELF-OPTIMIZING” CVs = Variables we can keep constant
WILL GET BACK TO THIS!
SOLUTION QUIZ 2
QUIZ. Assume low energy prices (pV=0.01 $/mol).
How should we control the columns?
HINT: CONTROL ACTIVE CONSTRAINTS
Hm…….
HINT: CONTROL ACTIVE CONSTRAINTS!

## Slide 53
Given
LC
LC
LC
LC
PC
PC
CC
xB
xBS=95%
MAX V1
MAX V2
CC
xAS (B) =2.1%
Control of Distillation columns. Cheap energy
Solution.
Notes: 53

## Slide 54: Comment: Distillation column control in practice
Add stabilizing temperature loops
  In this case: use reflux (L) as MV because boilup (V) may saturate
  T1s and T2s then replace L1 and L2 as DOFs.
Replace V1=max and V2=max by DPmax-controllers (assuming max. load is limited by flooding)
See next slide

## Slide 55: Control of Distillation columns in series
Given
LC
LC
LC
LC
PC
PC
TC
TC
T1s
T2s
T1
T2
Comment: In practice
MAX V2
MAX V1
CC
xB
xBS=95%

## Slide 56: Active constraint regions for two distillation columns in series
CV = Controlled Variable
3
2
0
1
1
0
2
[mol/s]
[$/mol]
1
Cheap energy: 1 remaining unconstrained DOF (L1)
-> Need to find 1 additional CVs (“self-optimizing”)
More expensive energy: 3 remaining unconstrained DOFs
-> Need to find 3 additional CVs (“self-optimizing”)
Energy
price
Distillation example: Not so simple
Mode 2: operate at BOTTLENECK
Higher F infeasible because
all 5 constraints reached
Mode 1

## Slide 57: How many active constraints regions?
Maximum:
  nc = number of constraints
BUT there are usually fewer in practice
Certain constraints are always active (reduces effective nc)
Only nu can be active at a given time
  nu = number of MVs (inputs)
Certain constraints combinations are not possibe
  For example, max and min on the same variable (e.g. flow)
Certain regions are not reached by the assumed disturbance set
Distillation
nc = 5
  25 = 32
xB always active
2^4 = 16
-1 = 15
In practice = 8

## Slide 58: More on: Optimal operation
Mode 1. Given feedrate
Mode 2. Maximum production
Comment: Depending on prices, Mode 1 may include many subcases (active constraints regions)
minimize J = cost feed + cost energy – value products
Two main cases (modes) depending on marked conditions:

## Slide 59: Mode 1. Given feedrate
Amount of products is then usually indirectly given and
Optimal operation is then usually unconstrained
“maximize efficiency (energy)”
Control:
Operate at optimal trade-off
NOT obvious what to control
CV = Self-optimizing variable
J = cost feed– value products + cost energy
c
J = energy
copt
Often constant

## Slide 60: Mode 2. Maximum production
Assume feedrate is degree of freedom
Assume products much more valuable than feed
Optimal operation is then to maximize product rate
“max. constrained”, prices do not matter
Control:
Focus on tight control of bottleneck
“Obvious what to control”
CV = ACTIVE CONSTRAINT
c
J
cmax
Infeasible
region
J = cost feed + cost energy – value products

## Slide 61
If constraint can be violated dynamically (only average matters)
  Required Back-off = “measurement bias” (steady-state measurement error for c)
If constraint cannot be violated dynamically (“hard constraint”)
  Required Back-off = “measurement bias” + maximum dynamic control error
Jopt
Back-off
Loss
c ≥ cconstraint
c
J
More on: Active output constraints
Need back-off
  Want tight control of hard output constraints to reduce the back-off. “Squeeze and shift”-rule
The backoff is the “safety margin” from the active constraint and is defined as the difference between the constraint value and the chosen setpoint
Backoff = |Constraint – Setpoint|
CV = Active constraint

## Slide 62
Hard Constraints: «SQUEEZE AND SHIFT»
CV = Active constraint

## Slide 63: Hard Constraints: «SQUEEZE AND SHIFT»
© Richalet
SHIFT
SQUEEZE
CV = Active constraint
Rule for control of hard output constraints:
“Squeeze and shift”!
Reduce variance (“Squeeze”) and “shift” setpoint cs to reduce backoff

## Slide 64
Example. Optimal operation = max. throughput. Want tight bottleneck control to reduce backoff!
Time
Back-off
= Lost production
CV = Active constraint

## Slide 65: Example back-off. xB = purity product > 95% (min.)
D1 directly to customer (hard constraint)
  Measurement error (bias): 1%
  Control error (variation due to poor control): 2%
  Backoff = 1% + 2% = 3%
  Setpoint xBs= 95 + 3% = 98% (to be safe)
  Can reduce backoff with better control (“squeeze and shift”)
D1 to large mixing tank (soft constraint)
  Measurement error (bias): 1%
  Backoff = 1%
  Setpoint xBs= 95 + 1% = 96% (to be safe)
  Do not need to include control error because it averages out in tank
CV = Active constraint
D1
xB
8
xB
xB,product
±2%

## Slide 66: Unconstrained optimum: Control “self-optimizing” variable.
Which variable is best?
Often not obvious (marathon runner)

## Slide 67
Q1: I have to set back-off on output active constraints, right? Should I set it before evaluating losses? How much back-off should be set, 5%?
[Sigurd Skogestad] 5% is a good start, but it depends mostly on the measurement accuracy. Note that it must be a hard output constraint.
The value of the active constraint is usually considered a disturbance; this also takes care of the backoff variation
Q2: When I consider input active constraints as disturbance too. Ex. Temp feed to SOFC (T0f, T0a) are active at upper bound. Should I set +10% on this disturbance change or just -10%.
Is it possible to set +10% in this case?
[Sigurd Skogestad] Yes, the actual available input could be larger than what you think
Q3: In region I, I would like to try same structure as in region II which means Uf,MCFC set at 75% (upper bound) but it is an input active constraint
which considered as disturbance too. Hence Uf,MCFC doesn’t a disturbance in region I, am I right? Then region I have 4 disturbances but region II and III have 5 disturbances, am I right?
[Sigurd Skogestad] No, because also the value of the active constraint is usually considered as a disturbance
Q4: Do I need back-off on input active constraints too?
Answer: Input constraint: Normally not, except of it is a bottleneck constraint and the TPM is located somewhere else

## Slide 68: More on: WHAT ARE GOOD “SELF-OPTIMIZING” VARIABLES?
Intuition: “Dominant variables” (Shinnar)
More precisely
  Optimal value of CV is constant
  CV is “sensitive” to MV (large gain)
Unconstrained variables

## Slide 69: GOOD “SELF-OPTIMIZING” CV=c
Optimal value copt is constant (independent of disturbance d):
  c is “sensitive” to MV=u (to reduce effect of measurement noise)
Equivalently: Optimum should be flat
Unconstrained optimum
BAD
Good
Good

## Slide 70: Conclusion optimal operation
ALWAYS:
1. Control active constraints and control them tightly!!
  Good times: Maximize throughput -> tight control of bottleneck
2. Identify “self-optimizing” CVs for remaining unconstrained degrees of freedom
Use offline analysis to find expected operating regions and prepare control system for this!
  One control policy when prices are low (nominal, unconstrained optimum)
  Another when prices are high (constrained optimum = bottleneck)
ONLY if necessary: consider RTO on top of this

## Slide 71: Sigurd’s rules for CV selection
Always control active constraints! (almost always)
Purity constraint on expensive product always active (no overpurification):
  (a) "Avoid product give away" (e.g., sell water as expensive product)
  (b) Save energy (costs energy to overpurify)
Unconstrained optimum:
Look for “self-optimizing” variables. They should
  Be sensitive to the MV
  have close-to-constant optimal value
NEVER try to control a variable that reaches max or min at the optimum
  In particular, never try to control directly the cost J
  Assume we want to minimize J (e.g., J = V = energy) - and we make the stupid choice os selecting CV = V = J
    Then setting J < Jmin: Gives infeasible operation (cannot meet constraints)
    and setting J > Jmin: Forces us to be nonoptimal (which may require strange operation)