## Slide 1: Standard Advanced control elements
Each element links a subset of inputs with a subset of outputs
Results in simple local tuning
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages).

## Slide 2: MV-CV Pairing. Two main pairing rules (supervisory layer*):
“Pair-close rule” : The MV should have a large, fast, and direct effect on the CV.
“Input saturation rule”: Pair a MV that may saturate with a CV that can be .given up (when the MV saturates).*
  Exception: Have extra MV so we use MV-MV switching (e.g., split range control)
“ RGA-rule”
  Avoid pairing on negative steady-state RGA-element. Otherwise, the loop gain may change sign (for example, if the input saturates) and we get instability with integral action in the controller.
Most basic element: Single-loop PID control (E0)
Additional rule for interactive systems:
*For regulatory (stabilizing) control, we usually want to avoid using any MV that may saturate (so Rule 2 becomes: Avoid using a MV that may saturate), but for the supervisory layer this is not possible

## Slide 3: Details on RGA-rule
S. Skogestad & I. Postlethwaite, Multivariable feedback control, 2nd Edition, Wiley, 2005

## Slide 4: Most common “Advanced regulatory control” structures
Used when single-loop feedback control (PID) alone is not good enough
Cascade control (measure and control internal variable) E1
Feedforward control (measure disturbance, d) E11
    (Very*) special case: ratio control E2
Extra MV dynamically: Valve position control E3
    Also known as input resetting or midranging
Change in CV: Selectors (max, min) E4
Extra MV steady state: Split range control (+2 alternatives) E5 (+E6, E7)
All of these are extensively used in practice, but little academic work
*Ratio control is a «very» special case of feedforward because it requires no model for the output (property) y we want to control.

## Slide 5: Standard advanced control elements
E1-E18

## Slide 6: E1. Cascade control
General case (“parallel cascade”)
Special common case (“series cascade”)
Not always helpful…
y2 must be closely related to y1
Master controller
Slave controller
1 input u
1 (main) output y1
1 extra measurement y2
Key assumption: Control of y2 indirectly makes it easier to control y1
Solution: Primary controller (master) controls y1 by setting setpoint r2=y2sp to a fast secondary controller (slave) which manipulates u

## Slide 7: Example: Flow controller on valve (very common!)
Helpful to reduce valve nonlinearity and provide local disturbance rejection (d=p1, p2)
  y = level H in tank (or could be temperature etc.)
  u = valve position (z)
  y2 = flowrate q through valve
LC
H
Hs
flow in
flow out
MV=z
valve position
WITHOUT CASCADE
WITH CASCADE
measured
flow
LC
H
Hs
flow in
flow out
MV=qs
FC
q
z
master
slave
p1 p2

## Slide 8: What are the benefits of adding a flow controller (inner cascade)?
q
z
qs
Counteracts nonlinearity in valve, f(z)
  With a fast flow controller we can assume q = qs (in spite of nonlinearity in the valve)
Eliminates effect of disturbances in p1 and p2
(FC reacts faster than outer level loop)
Extra measurement y2 = q
z
(valve opening)
f(z)
0
1
0
1
linear valve

## Slide 9: Block diagram flow controller
Example: Level control with slave flow controller:
u = z (valve position, flow out)
y1 = H
y2 = q
d’1 = flow in
d2 = p1-p2
Transfer functions:
G2 = k(z)/(τs+1) where k(z) = dq/dz (nonlinear!)
G1 = - 1/(As)
K1 = Level controller (master)
K2 = Flow controller (slave)
p1
p2
Valve
di1
f(z)
0
1
0
1
linear valve
k(z) = slope df/dz
di2

## Slide 10: Shinskey (1967)

## Slide 11: When use (series) cascade ?
Use cascade control (with an extra secondary measurement y2) when one or more of the following occur:
Significant disturbances d2 and di2 inside slave loop (and y2 can be controlled faster than y1)
The plant G2 is nonlinear or varies with time or is uncertain.
Measurement delay for y1
  Note: In the flowsheet above, y1 is the measured output, so any measurement delay is included in G1
Integrating dynamics (including slow dynamics or unstable) in both G1 and G2, (because without cascade a double integrating plant G1G2 is difficult to control)
Design / tuning
First design K2 (“fast loop”) to deal with d2 and di2 (based on model G2)
Then, with K2 closed, design K1 to deal with d1 and di1 (based on model G1T2)
Slave
controller
Master
controller
di1
di2

## Slide 12: Transfer functions and tuning
T2
d’1
First tune fast inner controller K2 (“slave”)
  Design K2 based on model G2
  Select τc2 based on effective delay in G2
  Transfer function for inner loop (from y2s to y2): T2 = G2 K2/(1+G2 K2)
  Because of integral action, T2 has loop gain = 1 for any G2.
  With SIMC we get: T2 e-ϴ2s/(τc2s+1)
  Nonlinearity: Gain variations (in G2) translate into variations in actual time constant τC2 (see next page)
Then with slave closed, tune slower outer controller K1 (“master”):
  Design K1 based on model G1’=T2*G1
  Can often set T2=1 if inner loop is fast!
  Alternatively, T2 e-ϴ2s/(τc2s+1) e-(ϴ2+τc2)s
  Even more accurate: Use actual T2 (normally not necessary)
  Typical choice: τc1 = τc2 where time scale separation

## Slide 13: Time scale separation is needed for cascade control to work well
Inner loop (slave) should be at least 4 times* faster than the outer loop (master)
  This is to make the two loops (and tuning) independent.
  Otherwise, the slave and master loops may start interacting
    The fast slave loop is able to correct for local disturbances, but the outer loop does not «know» this and if it’s too fast it may start «fighting» with the slave loop.
But normally recommend 10 times faster,
  A high σ is robust to gain variations (in both inner and outer loop)
  The reason for the upper value (σ =10) is to avoid that control gets too slow, especially if we have many layers
* Shinskey (Controlling multivariable processes, ISA, 1981, p.12)

## Slide 14
XC
TC
FC
ys
y
Ls
Ts
L
T
z
XC
Cascade control distillation
3 layers of cascade
With flow loop +
T-loop in top
τc=15s
τc=150s
τc=1500s
=25 min
Problem with many layers:
Eats up the time window

## Slide 15: Counteracting nonlinearity using cascade control
Example: Consider slave flow controller with u = z (valve position) and y2 = q (flow)
  Nonlinear valve with varying gain k2: G2(s)= k2(z) / (s+1)
  Slave (flow) controller K2: PI-controller with gain Kc2 and integral time I= (SIMC-rule). Get
  With slave controller: Transfer function from y2s to y2 (as seen from outer loop):
T2 = L2/(1+L2) = 1/(C2 s + 1), where C2 = /(k2 Kc2)
Important: Gain for T2 is always 1 (independent of k2) because of intergal action in the inner (slave) loop
But: Gain variation in k2 (inner loop) translates into variation in closed-loop time constant C2. This may effect the master loop:
  The master controller K1 is designed based on G1T2.
  A smaller process gain k2 results in a larger C2 and thus a large effective delay, whuch mat be bad.
    Recall T2 e-ϴ2s/(τc2s+1) e-(ϴ2+τc2)s
  However, if the time scale separation σ is sufficiently large, the variations in C2 will not matter
f(z)
0
1
0
1
linear valve
k2(z) = slope = df/dz
G1T2 = «Process» for tuning master controller K1

## Slide 16: Cascade control block diagram
Which disturbances motivate the use of cascade control?
C1
C2
P2
P1
+
d2
r1
y1
r2
u
y2
+
d1
+
d1o
Answer: d2

## Slide 17: E2. Ratio control
Special (and most common) case of feedforward
Example: Process with two feeds F1 (d) and F2 (u), where ratio should be constant.
Use multiplication block:
x
(F2/F1)s
F1
(measured flow
disturbance)
F2
(MV: manipulated variable)
Often (F2/F1)s is adjusted using feedback control in a cascade fashion.

## Slide 18
Flour
(solid)
Viscosity y [cP]
y
∞
Product
Water
FC
x
R=(F2/F1)s
u= F2,s
d=F1,m
F2,m
VC
ym
ys
RATIO CONTROL
with outer feedback trim (to adjust ratio setpoint)
EXAMPLE: CAKE BAKING MIXING PROCESS

## Slide 19: Ratio control
Avoid divisions in implementation! (avoid divide by 0)
Process control textbooks has some bad/strange suggestions, for example, division (bad) and “ratio stations” (complex):
Bad solution
Avoid divisions (divide by 0 if u =0, for example, at startup)
This is complicated. What is RS?
Ok if implemented as shown in red at right
Seborg:

## Slide 20: Theory of Ratio control
Assumes that «scaling property» holds (physical insight): Keep ratio R (between extensive variables) constant in order to keep property y constant
  y: (any!) intensive variable
Implementation
  Feedforward: R=u/d
  Decoupling: R=u1/u2
    u,d: extensive variables
  Setpoint for R may be found by «feedback trim»
Don’t really need a model (no inverse as in «normal» feedforward!)
Scaling property holds for mixing and equilibrium processes
    Rato control is almost always used for mixing of reactants
  Requires that all extensive variables are scaled by same amount
    So does not hold for heat exchanger (since area A is constant) or non-equilibrium reactor (since volume V is constant)
    So should not keep L/F constant for distillation column with saturated (max) heat input (V)

## Slide 21: From paper by Skogestad (2023)

## Slide 22
Flour
(solid)
Viscosity y [cP]
y
∞
Product
Water
FC
x
R=(F2/F1)s
u= F2,s
d=F1,m
F2,m
VC
ym
ys
LINEARITY OF RATIO CONTROL: This way of implementing ratio control makes it easy to tune the outer feedback loop (VC controller) because
The gain from MV = Rs to CV=y (here viscosity) does not depend on the disturbance d=F1.
Proof: This is general for this way of implanting ratio control, because a given change in R has the same effect on the property y, independent of the total flow is.
Implementation of ratio control: u = R d (in unscaled/physical units)

## Slide 23: Proof of constant gain for ideal mixing
-
Ideal mixing: The property y depends linearly on composition c, , so we just need to show that the gain from MV=R to composition c is independent of the total flow.
Proof. The component balance gives: CV=c=(c1F1 + c2F2)/(F1+F2)
We are here considering disturbances in F1, so assume that c1 and c2 are constant.
We also assume that there is an outer loop so that c remains constant. From the component balance we see that c=constant implies that at as we change F1 (disturbance) we will have that R=F2/F1=constant.
With no ratio control: The gain from MV=F2 to CV=c is:
  K = (c2-c1)F1/(F1+F2)^2 = (c2-c1)/[(1+R)(F1+F2)]
  With R=constant (ats teady state) we then have K = constant/(F1+F2) so the gain K will change with operation, which will be a problem for the outer feedback controller (CC). Actually, we find that K=infinity when F=F1+F2 goes to zero, so we may get instability in the outer feedback loop at low flowrates.
With ratio control: The gain from MV=Rs=(q2/q1)s to CV=c is:
  Kr = (c2-c1)F1^2/(F1+F2)^2 = (c2-c1) /(1+R)2
  With R=constant (at steady state) we get Kr= constant independent of the value of the disturbance (F1)! So the outer loop always has the same gain and there no reason to be careful about the tunings.
Note: An alternative to ratio control is “standard” feedforward control where u = uFB + uFF (where FB is from the feedback controller CC and FF is from a feedforward controller from d=F1.) In this case we get the problem with process gain variation for the feedback controller CC). So ratio control is the best!

## Slide 24: Valve position control (VPC)
Have extra MV (input): One CV, many MVs
Process
Two different cases of VPC:
E3. Have extra dynamic MV
  Both MVs are used all the time
E7. Have extra static MV
  MV-MV switching: Need several MVs to cover whole range at steady state
  We want to use one MV at a time

## Slide 25: E3. VPC for extra dynamic input
Alternative term for dynamic VPC:
Mid-ranging control (Sweden)
u2 = main input for steady-state control of CV
(but u2 is poor for directly controlling y
  e.g. time delay or u2 is on/off )
u1 = extra dynamic input for fast control of y
VPC
Process
u1
u2
y
Example 1: Large (u2) and small valve (u1) (in parallell) for controlling total flowrate (y=F)
  The large valve (u2) has a lot of stiction which gives oscillations if used alone for flow control
  The small valve (u1) has less stiction and gives good flow control, but it’s too small to use alone
Example 2: Strong base (u2) and weak base (u1) for neutralizing acid (disturbance) to control y=pH
  Do pH change gradually (in two tanks) with the strong base (u2) in the first tank and the weak base (u1) in the last tank. u1 controls the pH in the last tank (y)

## Slide 26: Example: Heat exchanger with bypass
Want tight control of y=T.
u1=zB (bypass)
u2=CW
Proposed control structure?
zB
T

## Slide 27: Attempt 1. Use u2=cooling water: TOO SLOW
zB=0 (closed)
T
TC

## Slide 28: Attempt 2. Use u1=zB=bypass. SATURATES (at zB=0=closed if CW too small)
T
TC
=constant
zB
Advantage: Very fast response (no delay)
Problem: zB is too small to cover whole range
+ not optimal to fix at large bypass (waste of CW)

## Slide 29: What about VPC?
Want tight control of y=T.
u1= zB
u2=CW
Proposed control structure?
Main control: u2=CW
Fast control: u1=zB
zB
T

## Slide 30: Attempt 3 (proposed): VPC
T
TC
zB
SP=50%
VPC
Fast control of y: u1 = zB
Main control (VPC): u2=CW (slow loop)
Need time scale separation between the two loops

## Slide 31: Comment on heat exchanger example
The above example assumes that the flows on the two sides are «balanced» (mcP for cooling water (CW) and hot flow (H) are not too different) such that both the bypass flow (u1) and CW flow (u2) have an effect on T (CV)
There are two «unbalanced» cases:
  If CW flow is small, then T-outCW will always approach T-inH, so from a total energy balance, the bypass will have almost zero steady-state effect on T.
  If CW flow is large, then T-outH (before bypass mixing point) will always approach T-inCW, so CW will have almost zero effect on T. (both steady state and dynamically)
This illustrates that heat exchanger may behave very nonlinearly, and a good control structure for one heat exchanger case, may not work well for another case

## Slide 32: Alternative to VPC: Parallell control

## Slide 33: VPC with one MV: Stabilizing control with resetting of MV
Note: u is both an MV and a CV
VPC
Reservoir
Two-phase flow: Liquid and gas

## Slide 34: Example: Anti-slug control

## Slide 35: Example: Anti-slug control
Simulation without VPC (the system is unstable before PC is turned on):

## Slide 36: Example: Anti-slug control

## Slide 37: Example: Stabilize bycycle
Espen Storkaas and Sigurd Skogestad, "Cascade Control of unstable systems with application to stabilization of slug flow", IFAC-symposium Adchem'2003, Hong Kong, Presented: Jan. 2004 (original conference date: June 2003.)
Comment: Another example is a motorcycle where tilting is required for making turns.

## Slide 38: Constraint switching (because it is optimal at steady state)
CV-CV switching
  Control one CV at a time
MV-MV switching
  Use one MV at a time
MV-CV switching
  MV saturates so must give up CV
  Simple («do nothing») and
  Complex (repairing of loops)
Process
Process
Process
Process

## Slide 39: E4. Selector (for CV-CV switching*)
Many CVs paired with one MV.
But only one CV controlled at a time.
Use: Max or Min selector
Sometimes called “override”
  But this term may be misleading
Selector is generally on MV (compare output from many controllers)
Process
Note: Selectors are logic blocks
*Only option for CV-CV switching. Well, not quite true: Selectors may be implemented in other ways, for example, using «if-then»-logic.

## Slide 40: Implementation selector
Alt. I (General). Several controllers (different CVs)
    Selector on MVs
      Must have anti windup for C1 and C2 !
Alt. II (Less general) Controllers in cascade
    Selector on CV setpoint
    Good alternative if CVs (y1 and y2) are related so that cascade is good
    In this case: Selector may be replaced by saturation element
    (with y2s as the max or min)
Alt. III (For special case where all CVs have same bound). One controller
    Selector is on CVs (Auctioneering)
    Also assumes that dynamics from u to y1 and y2 are similar; otherwise use Alt.I
    Example: Control hot-spot in reactor or furnace.
>
y1
y2
y=max(y1,y2)
c
u
ys
Process
u
y1
y2
…
u=max(u0,u1,u2)

## Slide 41: Example Alt. III
Hot-spot control in reactor or furnace
>
T1
T2
.
.
.
Tn
y=max(Ti)
C
u=Q
Comment: Could use General Alternative I (many controllers) for hot-spot control, with each temperature controller (c1, c2,…) computing the heat input (u1=Q1, u2=Q2, ….) and then select u = min(u1, u2, …), but it is more complicated.
CV-CV switching

## Slide 42: Furnace control
TC
u=Fuel gas
Flue gas
Process fluid (water)
Air
T1s = 500C
TC
T2max=700C
y1=T1
u1
u2
u=min(u1,u2)
Input (MV)
u = Fuel gas flowrate
Output (CV)
y1 = process temperature T1
(desired setpoint or max constraint)
y2 = furnace temperature T2
(max constraint)
Rule: Use min-selector for constraints that are satisfied with a small input
CV-CV switching
u = input = manipulated variable (MV)
y = output = controlled variable (CV)
MIN
with safety constraint (Alt. I)
y2=T2
HP steam

## Slide 43: Furnace control with cascade (Alt. II, selector on CV-sp)
TC
u=Fuel gas
Flue gas
Process fluid
Air
T1s = 500C
TC
T2max = 700C
MIN
y1=T1
y2=T2
u1
u2
CV-CV switching, alternative solution
T2s
Comparison
The cascade solution is less general but it may be better in this case.
Why better? Inner T2-loop is fast and always active and may improve control of T1.
Comment: For both Alt. I and II, we loose control of T1 (it drops below T1s=500C) when T2=T2max. If this is not acceptable then we need to something- More on this later!

## Slide 44: Example Alt. I (Choke valve)
The choke valve is normally fully open to avoid unnecessary pressure drop (normally, we may have p1=4.5 bar, p2=4 bar)
But may close choke valve to avoid too low p1 (if N2 supply stops) or too high p2 (if p1 is high).
Here Alt. II (cascade) should not be used (Why? Cascade control makes it necessary to have one loop slow, which makes little sense since control of p1 does not improve control of p2 (or vice-versa).
Comment 1: Strictly speaking. the input u0=100% to the min-block is not needed, since the valve has a “bulit-in” min-selector at fully open (see later). But including it is not wrong - and it shows more clearly that we normally want u0=100%.
Comment 2: There may be quite a lot of interaction between the pressure and flow control. The best solution is probably to make one fast and one slow. In this case, it seems most reasonable to make the pressure control fast. But if fast flow control is needed, we may do it opposite.
Comment 3: I here use the term “choke valve” when the aim is to regulate pressure; and “control valve” when it is to regulate flow (but other people may not agree on this)
CV-CV switching

## Slide 45: Distillation example
Always control xD at constraint
(valueable product) to
avoid «product give-way»
May overpurity bottom to get more of the valuable product
(Alt. II: Selector on setpoint)
Avoid flooding using constraint on DP
(Alt. I: selector in input)
Note: A selector where one input is a constant (like the max-block for xB) may be replaced by a saturation element
CV-CV switching
From RTO

## Slide 46: Design of selector structure
Rule 1 (max or min selector)
Use max-selector for constraints that are satisfied with a large input
Use min-selector for constraints that are satisfied with a small input
Rule 2 (order of max and min selectors):
If need both max and min selector: Potential infeasibility (conflict)
Order does not matter if problem is feasible
If infeasible: Put highest priority constraint at the end
“Systematic design of active constraint switching using selectors.”
Dinesh Krishnamoorthy , Sigurd Skogestad. Computers & Chemical Engineering, Volume 143, (2020)
CV-CV switching

## Slide 47: Rule 2 (order of selectors)

## Slide 48: Example. Maximize flow with pressure constraints
Op
Input u = z1
Want to maximize flow, J=-F:
CV-CV switching
The two p1-constraints are not conflicting, because they are on the same variable.
However the Fmax-constraint and p1min-constraint may be conflicting: Must choose which is most important.

## Slide 49
Disturbances in p0 and p2 (unmeasured)
CV-CV switching

## Slide 50
t>1800: u=zmax=1
CV-CV switching

## Slide 51: Valves have “built-in” selectors
Rule 3 (a bit opposite of what you may guess)
  A closed valve (umin=0) gives a “built-in” max-selector (to avoid negative flow)
  An open valve (umax=1) gives a “built-in” min-selector
  So: Not necessary to add these as selector blocks (but it will not be wrong).
  The “built-in” selectors are never conflicting because cannot have closed and open at the same time
  Another way to see this is to note that a valve works as a saturation element
CV-CV switching
Saturation element may be implemented in three ways (equivalent because never conflict)
Min-selector followed by max-selector
Max-selector followed by min-selector
Mid-selector

## Slide 52: Quiz. Is this OK?
Cristina: I am looking at a control solution using selectors for keeping the pressure within constraints, while maximizing the valve opening. See figure This is for the valve before a steam turbine. This should work OK, right? Of course, if pmax is reached while the valve is fully open, the turbine bypass will have to open.
Answer:
Rule 1. Yes, the rule is to use a max-selector for a constraint which is satisfied with a large input.
And since the pressure is measured upstream, the pressure will get lower if we increase the valve opening, making it easier to satisfy the pmax-constraint. So yes, this is OK.
Rule 1. Similar for the min-block with pmin.
Rule 2. Since you have two constraints on the same variable, you cannot have infeasibility so the order of the min. and max-blocks doesn’t matter for pmin and pmax.
Rule 2. Yes, the desired value uo=zmax should always enter the first block.
Conclusion: yes, it works.
BUT….
Comment 1: But note that there is also a “hidden” min-selector just before the valve because of the valve which has zmax. And also a “hidden” max-selector because of zmin (a fully closed valve). These constraints may be inconsistent with the pressure constraints.
Comment 2: Since the order of the two selectors does not matter in this case, one may instead use the “equivalent” alternative with the max-block first. But we then see clearly that the constraint on pmax will never be activated, because ztmax is large. I guess this makes sense since you want to have the valve as open as possible, so then the you will always be at the pmin-constraint or have a fully open valve. So you can cut the pmax-constraint (and thus the max-selector) as you anyway want to open the valve as much as possible.
In addition, you can also cut the min-selector because there is already a “hidden” min-selector with zmax. (On the other hand, it will not be wrong to keep them.)
CV-CV switching
Final conclusion: Yes, it works, but it’s much too complicated.
All what is shown can be replaced by a pressure controller (PC) with setpoint pmin.

## Slide 53: E5. Split-range control (SRC) (for MV-MV switching)
For MVs (u) that have same effect (same sign) on the output (y) (Fig. 21), we need to define the order in which the MVs will be used. This is done by the order in in the SR-block.
Example: With two heating sources, we need to decide which to use first (see next Example)
Advantage: SRC is easy to understand and implement!
Disadvantages:
Only one controller C Same integral time for all inputs ui (MVs)
  Controller gains can be adjusted with slopes in SR-block!
Does not work well for cases where constraint values for ui change

## Slide 54: Challenges selectors
Standard approach requires pairing of each active constraint with a single input
  May not be possible in complex cases
  See RTO/feedback-based RTO
Stability analysis of switched systems is still an open problem
  Undesired switching may be avoided in many ways:
    Filtering of measurement
    Tuning of anti-windup scheme
    Minimum time between switching
    Minimum input change
CV-CV switching

## Slide 55: Split range control: Donald Eckman (1945)
MV-MV switching

## Slide 56
MVs (two for summer and two for winter):
AC (expensive cooling)
CW (cooling water, cheap)
HW (hot water, quite cheap)
Electric heat, EH (expensive)
y=T
Example split range control: Room temperature with 4 MVs
MV-MV switching
SR-block:
1
3
2
4
CPI – same controller for all inputs (one integral time)
But get different gains by adjusting slopes α in SR-block

## Slide 57
Simulation Split-range control (SRC)
MV-MV switching
summer
winter
y=T
1
3
2
4
d=Tamb

## Slide 58
Alternative: Generalized SRC (Baton strategy: multiple independent controllers)
Disadvantages Standard Split-range control (SRC):
Must use same integral/derivative time for all MVs
Does not work well when constraint values change (SR-block problem)
MV-MV switching
y=T
A. Reyes-Lúa and S. Skogestad. “Multi-input single-output control for extending the operating range:
Generalized split range control using the baton strategy”. Journal of Process Control 91 (2020)
d=Tamb
All four controllers need anti-windup

## Slide 59
Disadvantages Standard Split-range control (SRC):
Must use same integral/derivative time for all MVs
Does not work well when constraint values change (SR-block problem)
MV-MV switching
y=T
A. Reyes-Lúa and S. Skogestad. “Multi-input single-output control for extending the operating range:
Generalized split range control using the baton strategy”. Journal of Process Control 91 (2020)
d=Tamb
All four controllers need anti-windup
Alternative: Generalized SRC (Baton strategy: multiple independent controllers)

## Slide 60: Comparison of standard and generalized SRC
Generalized split range control:
Different (smaller) integral times for each input
Gives faster settling for most inputs
A. Reyes-Lúa and S. Skogestad. “Multi-input single-output control for extending the operating range:
Generalized split range control using the baton strategy”. Journal of Process Control 91 (2020)
MV-MV switching

## Slide 61: What about Model Predictive control (MPC)?

## Slide 62: Comparison of Generalized SRC and MPC
Responses
MPC: Similar response to standard SRC
MPC: Faster initially, uses several input simultanously
MPC: Slower settling
Disadvantage MPC:
Complex: Requires full dynamic model
Does not use on input at a time
A. Reyes-Lúa and S. Skogestad. “Multi-input single-output control for extending the operating range:
Generalized split range control using the baton strategy”. Journal of Process Control 91 (2020)
MV-MV switching

## Slide 63: E6. Separate controllers with different setpoints (for MV-MV switching)
Advantages E6 (compared to split range control, E5):
Simple to implement (no logic)
Controllers can be tuned independently (different integral times)
Switching by feedback: Do not need to know constraint values
  Big advantage when switching point varies (complex MV-CV switching)
Disadvantages:
Temporary loose control during switching
Setpoint not constant
  Can be an advantage (for example, may give energy savings for room heating)
Comment on the blue blocks: Saturation can occur for any physical input, but they are explicitly shown for cases where the saturation is either the reason for or part of the control logic.

## Slide 64
MVs (two for summer and two for winter):
AC (expensive cooling)
CW (cooling water, cheap)
HW (hot water, quite cheap)
Electric heat, EH (expensive)
y=T
Alt. A2 for MV-MV switching. Multiple controllers with different setpoints
Example: Room heating with one CV (T) and 4 MVs
E6: MV-MV switching
Disadvantage (comfort):
Different setpoints
Advantage (economics) :
Different setpoints (energy savings)
C1
C2
C3
C4
23oC
22oC
21oC
20oC

## Slide 65
A Reyes-Lua, S Skogestad. Multiple-Input Single-Output Control for Extending the Steady-State Operating Range - Use of Controllers with Different Setpoints. Processes 7 (12), 941
y=T
1
3
2
4
d=Tamb

## Slide 66: Want separate controllers. Fixes that avoid using different setpoints
Alt.1: «Baton strategy» (a bit complicated).
Alt.2 (simpler, but gives temporary setpoint change at MV-MV switch): Introduce a (slow) outer cascade (master controller) that resets the setpoint of the active controller to ys, while maintaining the setpoint distances

## Slide 67: Fix: Outer cascade to avoid different setpoints

## Slide 68: E7. VPC on main steady-state input (for MV-MV switching)
VPC
Advantages E7 (for MV-MV switching): Always use u1 to control y
  For example, u2 may only allow discrete changes (e.g., u2=0,1,2,3)
  or dynamics for u2 may be very slow
Disadvantages E7:
We cannot let u1 become fully saturated because then control of y is lost
  This means that we cannot use the full range for u1 (potential economic loss)
Related: When u2 is used, we need to keep using a ‘‘little’’ of u1.
  Example: May need to use both heating and cooling at the same time (when u1 normally should be off).

## Slide 69: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=0.9 bar
=1 bar
=1.1 bar
=1 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q = z1
but if Q=0 (because of too hot feed) we must use MV3=vent =z3
and if Q=max (becase of too cold feed) we must use MV2=inert = z2
Alt.3: VPC (z2 and z3 could here be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q=0 (z1=0.1)
Use inert (z2) to avoid Q=max (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
Example: Heating water with intermediate storage. «Inert» could be HP steam.
MV-MV switching
Example: Heating water to 213C = Control steam pressure at 20 bar*.
«Inert» (z2) could be HP steam.
Hot water
Hotter water
* Rule of thumb: p[bar] = [T[C]/100]^4

## Slide 70: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=0.9 bar
=1 bar
=1.1 bar
=20 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q
but if Q=0 we must use MV3=vent
and if Q=max we must use MV2=inert
Alt.3: VPC (z2 and z3 could here be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q=0 (z1=0.1)
Use inert (z2) to avoid Q=max (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
MV-MV switching
Hotter water
Hot water

## Slide 71: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=19 bar
=20 bar
=21 bar
=20 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q
but if Q=0 we must use MV3=vent
and if Q=max we must use MV2=inert
Alt.3: VPC (z2 and z3 could here be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q=0 (z1=0.1)
Use inert (z2) to avoid Q=max (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
MV-MV switching
Hotter water
Hot water

## Slide 72: Example MV-MV switching: Pressure control (Alt. 3 may be the best in this case)
INERT
z2
z3
z3
z2
z3
=21 bar
=20 bar
=21 bar
=20 bar
z1
z2
z3
CV=p
MV1=heat (Q)
MV2=inert
MV3=vent
Normal: Control CV=p using MV1=Q
but if Q=0 we must use MV3=vent
and if Q=max we must use MV2=inert
Alt.3: VPC (z2 and z3 could here even be on/off valves)
Always use Q (z1) to control p.
Need two VPC’s:
Use vent (z3) to avoid Q small (z1=0.1)
Use inert (z2) to avoid Q large (z1=0.9)
z2=0 and z3=0 when 0.1<z1<0.9
MV-MV switching
=20 bar
Hotter water
Hot water

## Slide 73: Beware: Two different applications of VPC (E3 and E7)
The VPC schemes in Figure 12 (E3 - VPC on dynamic input) and Figure 24 (E7) seem to be the same
  In fact, they are the same - except for the blue saturation elements - which tells that in Figure 24 (E7) the saturation has to be there for the structure to work as expected
But their behavior is very different!
  In Figure 12 (E3) both inputs are used all the time
    u1 is used to improve the dynamic response
    u2 is the main steady-state input (and used all the time)
    u1s is typically 50% (mid-range)
  In Figure 24 (E7)
    u1 is the main input (and used all the time)
    u2 is only used when u1 approaches saturation (for MV-MV switching)
    The setpoint u1s is typically close to the expected saturation constraint (10% or 90%)
I frequently see people confuse these two elements -
which is very understandable!
E3 (Fig. 12)
E7 (Fig. 24)

## Slide 74: Summary MV-MV switching

## Slide 75: Summary MV-MV switching
Need several MVs to cover whole steady-state range (because primary MV may saturate)*
Note that we only want to use one MV at the time.
  Alt.1 Split-range control (one controller) (E5)
    Advantage: Easy to understand because SR-block shows clearly sequence of MVs
    Disdvantages: (1) Need same tunings (integral time) for all MVs . (2) May not work well if MV-limits inside SR-block change with time, so: Not good for MV-CV switching
  Alt.2 Several controllers with different setpoints (E6)
    Advantages: 1. Simple to implement, do not need to keep track of MVs. 2. Can have independent tunings. .
    Disadvantage: Setpoint varies (which can be turned into an advantage in some cases)
  Alt.3 Valve position control (E7)
    Advantage: Always use “primary” MV for control of CV (avoids repairing of loops)
    Disadvantages: Gives some loss, because primary MV always must be used (cannot go to zero).
Which is best? It depends on the case!
*Optimal Operation with Changing Active Constraint Regions using Classical Advanced Control, Adriana Reyes-Lua Cristina Zotica, Sigurd Skogestad, Adchem Conference, Shenyang, China. July 2018 ,
Process

## Slide 76: E8. Anti-windup for the integral mode
Without anti-windup:
With anti-windup using tracking:

## Slide 77: Anti-windup with cascade control
Inner loop
Outer loop
valve
Selector: y2s tracks y2 only when valve saturates*
u tracks
|.|
* The selector makes sure we use anti windup in the outer loop only when the inner loop (u) is saturating, and not just because the inner loop is a little slow.

## Slide 78: Why the selector? Cascade simulations from Greg McMillan to illustrate the «side effect» of anti-windup in the outer loop when using eT1=y2s-y2 all the time. tauT=tauI. (23 Jan. 2023)
This is the best
This is also good, because side effect is helping but just «by luck»
WITHOUT Anti-windup
WITH Anti-windup
Time scale separation = 5
Make outer loop even faster. Time scale separation = 2.5
Side-effect of anti-windup:
slows down I-action in outer loop.
Remedy: Select larger tauT
Oopss..
Oscillations (as expected)
The simulations with anti-windup are without the selector block on the previous page.
So the selector avoids the «side effect»!

## Slide 79: E9. Two degrees-of-freedom control
One degree-of freedom control: Controller uses e=ys-y
Two degrees-of freedom control: y and ys used differently.
  For example, no derivative action on setpoint,
  More generally, setpoint filter Fs:

## Slide 80: Measurement filter F(s)
Very common, especially with noisy measurements
  Used also alone (without Fs)
  Most common: First-order filter
  Recommended: (preferably smaller, typically )
  : Closed-loop time constant (SIMC)

## Slide 81: E10. Gain scheduling
Very popular for PID within EE and ME, e.g., airplanes, automotive.
Controller (PID) tunings change as a given function of the scheduling variable, e.g.,
  disturbance d
  process input u
  process output y
  setpoint ys
  control error e=ys-y

## Slide 82: E11. Feedforward control
Nonlinear feedforward based on input transformations (with setpoint v from feedback):
Linear feedforward, u = CFddm + c e
General: Feedforward inverts process:
Main problem feedforward:
  Sensitive to model error and changes (nonlinearity)
If perfect measurements: gm=1, gdm=1

## Slide 83
Avoid fighting of feedforward and feedback (with B)
Typically, for a setpoint change r, the feedforward block is A = G--1Fr where G- is the invertible part of G.
  A typical choice for the prefilter is Fr = 1/(τrs+1)
  Example. G=(-3s+1)exp(-4s)/(7s+1)^2, Fv=1 (perfect measurement) and taur=2. Use “IMC-like” design and write G = G+ G- where G+=exp(-4s)(-3s+1)/(3s+1) and G-=(3s+1)/(7s+1)^2. Gives A = (7s+1)^2/(3s+1)(2s+1)
We want to choose B such that A and K can be designed independently!!
  Solution* (Lang and Ham ,1955): Choose B=FyGA so that transfer function from r to the controller input (e) is zero (with perfect model) !!
  The feedback will then only take action if the feedforward is not working as expected (due to model error).
  We must have B(0)=I so that we will have no offset (y=r at steady state) even with model error for G
  Example. B(s) = FyGA = FyG+Fr = exp(-4s)(-3s+1)/(3s+1)(2s+1). Note that B(0)=1.
The feedback controller K can be designed for disturbance rejection and robustness, e.g., using SIMC rules.
  Example. Approximate as first-order with delay process with theta=4+3+7/2=10.5 and tau1=7+7/2=10.5, and use SIMC! With tauc=theta get Kc=0.5 and taui=10.5.
The same approach applies to disturbances (d=r) with a feedforward controller Cff and measurement Gdm, but then GA is replaced by (G Cff Gdm + Gd). So we get B = Fy (G Cff Gdm + Gd). Note that Fy=Gm in many cases.
e
*See my note on Two degrees …. in mlokal/sis Krister and….

## Slide 84
FIX
Example FF with B
CFF,ideal = - Gd/G = -es
Prediction; not possible, so use
CFF = -1
(SIMC)

## Slide 85: E12. Linear decoupling

## Slide 86: E13. Linearization elements
Typically, logarithm or nonlinear feedforward blocks
General approach: See Input transformations

## Slide 87: E14. Calculation block based on transformed input
SEE LATER

## Slide 88: E11. Simple static estimators
Inferential element
Soft sensor

## Slide 89: Additional standard elements
E16. Simple nonlinear static elements
  Multpliction
  Division (avoid or at least be careful)
  Square root
  Dead zone
  Dead band
  Limiter (saturation element)
  On/off
E17. Simple linear dynamic elements
  Lead-lag filter
  Time delay
  … more…
E18. Standard logic elements
  If, then, else
  Example: Select depending on sign of another signal:

## Slide 90: What about the Smith Predictor? Forget it!

## Slide 91: A smart invention: Cross-limiting control

## Slide 93: Comment on need for rules
The human brain (at least mine) has problems in analyzing even quite simple cases
Two «simple» cases are:
  choice of max- and min- selectors
  how to get consistent inventory control
I frequently need to og back to the «selector rules» or the «radiation rule» to get this right.