## Slide 1: Advanced control for the future using the magic of feedback and simple elements*
Sigurd Skogestad
Department of Chemical Engineering
Norwegian University of Science and Technology (NTNU)
Trondheim
17th Seminar on Power Electronics and Control (SEPOC) – November 9–12, 2025
"Applied Computing and Cutting-Edge Solutions in Power Electronics and Control for Industry 5.0"
Floranopolis
*a.k.a. Advanced regulatory control (ARC)

## Slide 2: Abstract
Advanced control refers to any control strategy that goes beyond basic single-loop PID control. It becomes necessary for processes involving multiple inputs, changing objectives or constraints, additional measurements, or measured disturbances. Many engineers intuitively think, “This is getting complicated—we need a model and optimization (e.g., MPC).” However, model-based control is often expensive to implement and highly sensitive to model uncertainty. Fortunately, there is a more robust yet less appreciated alternative: advanced PID architectures. These rely primarily on measurements (data) and feedback and consist of smart combinations of PID controllers with simple elements such as cascade control, selectors, split-range control, and ratio control.
My prediction: The future of advanced control will continue to be built on these simple PID architectures—just as they are today—despite having been largely neglected by academia for the past 80 years. Model-based control (e.g., MPC) will be added on top in specific applications, such as for strongly coupled processes or when future disturbances are known. Machine learning and AI (including tools like ChatGPT) are unlikely to be used extensively for real-time control, except in soft sensor (estimation) tasks. However, they will become important tools for offline tasks such as model development, software generation, control architecture design, and controller tuning.
Before ChatGPT: «Advanced control» is anything that comes in addition to single-loop PID control. It is needed for processes with extra inputs, changing control objectives and constraints, extra measurements and measured disturbances. The intuition of most engineers is that «this becomes very difficult, so we will need a model and optimization (MPC)». However, model-based control is costly to implement and sensitive to uncertainty. Fortunately, there is another option, mainly based on measurements (data) and feedback, which is much more robust but much less understood: Advanced PID-architectures that interconnect in a smart way PID controllers and other simple elements (cascade, selectors, split range control, ratio control).
My prediction: Advanced control in the future will use simple PID-architectures as the basis (as they do today - in spite of being neglected by academics for 80 years). It will be complemented with model-based control (MPC) for certain applications, for example, for strongly coupled processes or for cases where future disturbances are known. ML/AI will not be much used for online control, except for estimation (soft sensors). However, ML/AI (chatGPT) will be used for offline purposes, including developing models, writing software, suggesting control architectures and tuning controllers.

## Slide 3: Workshop on “Multivariable control Using Decomposition and Simple Elements"
How can you control a complex plant effectively using simple elements with a minimal amount of modelling? How can you put optimization into the control layer?
Industry has been using simple and effective “advanced regulatory control” (ARC) schemes for almost 100 years, yet they remain poorly understood and therefore underused. The objective of the workshop is to provide a systematic approach for designing such control systems. The target audience includes both practicing control engineers as well as PhD students and teachers from academia.
The workshop explores the standard advanced control elements commonly used in industry for designing advanced control systems. These elements include cascade, ratio, feedforward, decoupling, selectors, split range, and more, collectively referred to as "advanced regulatory control" (ARC). Numerous examples are provided, with a particular focus on process control. I emphasize the shortcomings of model-based optimization methods, such as model predictive control (MPC), and challenge the view that MPC can solve all control problems, while ARC solutions are outdated, ad-hoc and difficult to understand. On the contrary, decomposing the control systems into simple ARC elements is very powerful and allows for designing control systems for complex processes with only limited information. With the knowledge of the control elements presented in the workshop, participants should be able to understand most industrial ARC solutions (which can be a challenge!) and propose alternatives and improvements.

## Slide 4
Trondheim
Arctic circle
Geiranger fjord
Trondheim
Midnight or midday?

## Slide 5: About Sigurd Skogestad
•1955: Born in Flekkefjord, Norway
•1974-1978: MS (Siv.ing.) studies in chemical engineering at NTNU
• 1979: Military service (FFI)
•1980-1983: Worked at Norsk Hydro F-senter (process simulation)
•1983-1987: PhD student at Caltech (supervisor: Manfred Morari)
•1987-present: Professor of chemical engineering at NTNU
• 1994-95: Visiting Professor UC Berkeley
• 2001-02: Visiting Professor UC Santa Barbara
•1999-2009: Head of ChE Department, NTNU
•2015-.2023: Director SUBPRO (Subsea research center at NTNU)
Non-professional interests:
mountain skiing (cross country)
orienteering (running around with a map)
grouse hunting
1973

## Slide 6: “The goal of my research is to develop simple yet rigorous methods to solve problems of engineering significance”

## Slide 7: My research focus
Control for economic optimization
  Control of changing active constraints
Control for linearization, stabilization and robustness
Keep it simple!
  Make use of the magic of feedback

## Slide 8: October 1984 Robust control takes off!

## Slide 10: Robust control
1996
2005
Berkeley, Dec. 1994

## Slide 11
IMC PID tuning rule
(1984, 1986)

## Slide 12
Tuning parameter:
SIMC* PID tuning rule (2001,2003)
*SIMC = Simple/Skogestad IMC
=λ

## Slide 13: What is control? Generating actions u from measurements w (data) to stay at setpoint ys
w
measured online data
Want: y = ys
1. Feedback: w=ys-y
      P-control (negative feedback):
      Good control (): Need gain
      Don’t need accurate value for (but too large gives instability)
2. Feedforward: w=d or ys
      Perfect feedforward:
      Good control (): Need accurate model ()
Controller
(algorithm)
Process G
u
Actions (MVs)
y
d

## Slide 14: Feedforward versus feedback Example: Setpoint response
    Identical nominally
    Change process gain from k=3 to k’=4.5
    This can be achieved both with feedback (PI) and feedforward (nominally):
G(s)
u
y
CFy(s)
ys
u
G(s)
u
y
C(s)
ys
With MPC: Not clear which solution you get
Feedforward is sensitive to model error
(speed up a little)

## Slide 15: Feedback is needed / used for
Uncertainty about disturbances
Uncertainty in model
Linearization
Stabilization

## Slide 16: Linearizing effect of feedback

## Slide 17: The negative feedback amplifier
Amplification was required to send telephone signals across the US in the 1920s and it required 12 amplifications on the way, so they better be fairly accurate.
The original idea of all engineers is to think feedforward (Bell Labs)
Feedforward: Y = BAD y
With feedback: Y = (1/R) y (R: accurate resistance)
Harold Black (on a New York ferry, 02 August 1927):

## Slide 18
100
1000
10000
10
Bad amplifier:
Accurate resistance:
Get
Resulting amplification (negative feedback)
Experiment
Proving that Black’s invention worked also initiated the idea of freqyency analysis( Nyquist)

## Slide 19: Linearization of valve using cascade control
LC
y=H
Hs
flow in
flow out
MV=z
valve position
WITHOUT CASCADE
WITH CASCADE (2 controllers)
measured
flow
LC
Hs
flow in
flow out
MV=qs
FC
y2=q
MV2=z
master
slave
measured
level
measured
level
y=H
Benefits: 1. Local distrurbance rejection, 2. Linearization
Does nonlinearity disappear?

## Slide 20: No, it moves to the time constant of the slave loop – OK - if we we have time scale separation between master and slave
Nonlinear valve with varying gain k2: G2(s)= k2(z) / (s+1)
  Slave (flow) controller K2: PI-controller with gain Kc2 and integral time I= (SIMC-rule). Get
  With slave controller: Transfer function T2 from y2s to y2 (as seen from master loop):
T2 = L2/(1+L2) = 1/(C2 s + 1), where C2 = /(k2 Kc2)
Linearization: Gain for T2 is always 1 (independent of k2) because of intergal action in the inner (slave) loop
But: Gain variation in k2 (inner loop) translates into variation in closed-loop time constant C2. This may effect the master loop
f(z)
0
1
0
1
linear valve
k2(z) = slope = df/dz
G1T2 = «Process» for tuning master controller K1
Does nonlinearity disappear?

## Slide 21: Stabilization
The only way we can change dynamics (poles) and stabilize is by feedback
So: Stabilization with feedforward does NOT work
  Example: level control
    G(s) = k’/s
    Integrating process with pole at s=0. At the limit to instability
    It is practically impossible to control level by trying to set qout=qin using feedforward.
    We get «internal instability»: Level will eventually go out of bound
But we need to be careful: Feedback often causes oscillations and even instability

## Slide 22: Stabilization of the grid using P-control. Early 1930s
Initial idea (not workabler): Centralized coordination of power producers
1930s: Use grid frequency («level») as (local) measure of imbalance between supply and demand. And: Stabilize frequency using local P-control for all power producers
It’s the same as level control with many flows in and out
Need to have some back-off from maximum power for this to work (90%)
Many local P-controllers, but only one centralized I-controller
Centralized
I-control
Local
P-control

## Slide 23
y =
Frequency
or Level
Inflow
Inflow (producer)
Inflow
Outflow (consumer)
Outflow
ys = setpoint
Everyone contributes to stabilization of y

## Slide 24: Stabilization using feedback: Instability moves to input (RHP-zero)
General proof:

## Slide 25
Inverse response for bicycle / motorcycle caused by underlying instability
Move first in right direction
But end up moving in opposite direction

## Slide 26
Stabilization: Anti-slug control (IFAC, 2002)
Slug (liquid) buildup
Two-phase flow
(liquid and vapor)

## Slide 27: Anti slug-control - control structure
Slug-catcher
PIC
SP
PT
PT
Measurement y
Undesired slug flow (limit cycle) unless feedback
control is used to stabilize a steady flow regime
(desired, but open-loop unstable)

## Slide 28
Anti slug control – experimental data (Statoil/SINTEF)
Density
INPUT u
Pressure (y)
Controller ON
OFF

## Slide 29: Anti slug-control - control structure
Slug-catcher
PIC
SP
PT
PT
Input u =
Want open valve (80%)

## Slide 30: Anti slug-control - control structure
Slug-catcher
PIC
SP
PT
PT
VPC
SP=80%
VPC: Cannot be too fast because of
inverse response caused by underlying instability

## Slide 31: «Transformed inputs» v
Combining feedforward with feedback in an extremely simple way
Most effective for static feedforward
  Dynamic generalzation (= «feedback linearization») usually unrealistic because of many derivatives
Static model: y =f(u,d)
Select transformed inputs (= controller outputs): v = f(u,d)
Invert to get physical inputs: u = f-1(v,d)
Then response from v to y is: y= I v (linear, decoupled, perfect disturbance rejection)
FeedbackController
Calculation block (static FF)
Process
ys
y
V
d
u
y
Looks like magic but ut works
S. Skogestad, C. Zotica, N. Alsop., «Transformed inputs for linearization, decoupling and feedforward control», J. Proc. Control, 2023

## Slide 32: Example decoupling: Mixing of hot (u1) and cold (u2) water
Want to control
  y1 = Temperature T
  y2 = total flow F
Inputs, u=flowrates
May use two SISO PI-controllers
  TC
  FC
Insight: Get decoupled response with transformed inputs
  TC sets flow ratio, v1 = u1/u2
  FC sets flow sum, v2 = u1 + u2
Decoupler: Need «static calculation block» to solve for inputs
u1 = v1 v2 / (1+ v1)
u2 = v2 / (1 + v1)
T
F
u1
u2
v2=sum
v1=ratio

## Slide 33
TRANSFORMED INPUTS v=f(u,d): GENERAL APPROACH FOR COMBINED FEEDBACK,
FEEDFORWARD, DECOUPLING AND LINEARIZATION
Example: Mixing of hot and cold water
Controller
Calculation block (static)
Process
ys
y
V
d
u
y
Generalized ratio
Decoupler with feedforward:
It’s almost magic!

## Slide 34: How we design a control system for a complete chemical plant?
Where do we start?
What should we control? and why?
etc.
etc.
Sigurd at Caltech (1984)
Notes: 34

## Slide 35
A1: Benzene
A2: Ethylene
B: Ethylbenzene (product)
C: Diethylbenzene (undersired, recycled to extinction)
A1+A2 B
B + A2 C
C + A1
A1+A2 B
B + A2 C
C + A1
A1, A2 (recycle)
B (product)
C (recycle)
A2(feed)
A1(feed)

## Slide 36
Alan Foss (“Critique of chemical process control theory”, AIChE Journal,1973):
The central issue to be resolved ... is the determination of control system structure*. Which variables should be measured, which inputs should be manipulated and which links should be made between the two sets?
There is more than a suspicion that the work of a genius is needed here, for without it the control configuration problem will likely remain in a primitive, hazily stated and wholly unmanageable form.
The gap is present indeed, but contrary to the views of many, it is the theoretician who must close it.
Control system structure*
*Current terminology: Control system architecture
Notes: 36

## Slide 37
Alan Foss (“Critique of chemical process control theory”, AIChE Journal,1973):
The central issue to be resolved ... is the determination of control system structure*. Which variables should be measured, which inputs should be manipulated and which links should be made between the two sets?
There is more than a suspicion that the work of a genius is needed here, for without it the control configuration problem will likely remain in a primitive, hazily stated and wholly unmanageable form.
The gap [between theory and practice] is present indeed, but contrary to the views of many, it is the theoretician who must close it.
Control system structure*
*Current terminology: Control system architecture
Notes: 37

## Slide 38: Main objectives of a control system
Economics: Implementation of acceptable (near-optimal) operation
Regulation: Stable operation
ARE THESE OBJECTIVES CONFLICTING?
Usually NOT
  Different time scales
    Stabilization  fast time scale
  Stabilization doesn’t “use up” any degrees of freedom
    Reference value (setpoint) available for layer above
    But it “uses up” part of the time window (frequency range)

## Slide 39: Two fundamental ways of decomposing the controller
Vertical (hierarchical; cascade)
Based on time scale separation
Decision: Selection of CVs that connect layers
Horizontal (decentralized)
Usually based on distance
Decision: Pairing of MVs and CVs within layers
In addition: Decomposition of controller into smaller elements (blocks):
Feedforward element, nonlinear element, estimators (soft sensors), switching elements
PROCESS
CV = controlled variable MV = manipulated variable
MV

## Slide 40: Time scale separation: Control* layers
Two objectives for control: Stabilization and economics
Supervisory (“advanced”) control layer
Tasks:
  Follow set points for CV1 from economic optimization layer
  Switch between active constraints (change CV1)
  Look after regulatory layer (avoid that MVs saturate, etc.)
Regulatory control (PID layer):
  Stable operation (CV2)
CV = controlled variable
*My definition of «control» is that the objective is to track setpoints
PROCESS
setpoint
setpoint
MV

## Slide 41: «Advanced» control
Mainly used in the «supervisory» control layer
Two main options
  Standard «Advanced regulatory control» (ARC) elements
    This option is preferred if it gives acceptable performance
  Model predictive control (MPC)
    Requires a lot more effort to implement and maintain
  What about machine learning (AI)?
    No, it requires way too much data - would take years to learn
PROCESS
setpoint
setpoint

## Slide 42: Combine control and optimization into one layer?
CV = controlled variable
RTO = real-time optimization
PROCESS
setpoint
setpoint
Economic
cost J
EMPC
(no setpoints,
CV1, CV2)
JEMPC = J + Jcontrol
Penalize input usage, Jcontrol =
NO, combining layers is generally not a good idea!
(the good idea is to separate them!)
One layer (EMPC) is optimal theoreretically, but
Need detailed dynamic model of everything
Tuning difficult and indirect
Slow! (or at least difficult to speed up parts of the control)
Robustness could be poor
Implementation and maintainance costly and time consuming
EMPC: Economic model predictive “control”’
Typical economic cost function:
J [$/s] = cost feed + cost energy – value products

## Slide 43: Combine control and optimization into one layer?
CV = controlled variable
RTO = real-time optimization
Another thing: EMPC is not even control (for me).
My definition of «control» is that the objective is to track setpoints
I would call «Economic MPC» for «Dynamic economic optimization» or «Dynamic RTO»
I would not even call it «optimizing control»
  I use this term when the setpoints are directly related to economics,
  like control cost gradient to zero (Ju=0)
Conclusing EMPC: Use only when economics are truly dynamic (batch, frequent grade change)
PROCESS
setpoint
setpoint
Economic
cost J
EMPC: Economic model predictive “control”
EMPC
(no CV1)

## Slide 44: What about «conventional» MPC and RTO?
Yes, it’s OK
Has been around for more than 50 years (since 1970s)
But the expected growth never came:
  MPC is still used mostly in large-scale plants
    petrochemical (ammonia) and refineries
Also: MPC is not realistic for a new plant (need model)
Conclusion: MPC is far from replacing PID as some expected in the 1990s
  Need something else than conventional RTO/MPC!
MPC = model predictive control
RTO = real-time optimization

## Slide 45: A more fundamental problem with MPC / EMPC
All claimed stability results are «wrong»
They assume that we can measure all states perfectly
… or estimate them with a separate estimator block (LQG)

## Slide 46
John Doyle (1985):
There are two ways a theorem can be wrong
(from an engineering point of view):
Either it’s simply wrong
Or the assumptions make no sense
Fact:
Essentially all stability and convergence results for optimal control, MPC and nonlinear control assume full state information, that is, perfect measurement of all states (LQ-control)
Or they assume that one can simply add a Kalman filter for any unmeasured states (LQG)

## Slide 47
Practical «Solution» for some cases: Loop transfer recovery (LTR).
Artificial small weight on measurement noise to make estimator fast

## Slide 48: Doyle counterexample
G(s)
w
u
y
GML GM PM wc DM=PM/wc
LQG Doyle (w=1) 0.92 1.06 9 1.19 0.132
LQG Doyle (w=1e12) 0.904 1.0000007 18 3.97 0.252
SIMC-PID (tauc=0.1) 0.333 infinity 46 10.4 0.0774
%Process
A=[1 1; 0 1]; B=[0;1]; C=[1 0]; D=0;
SYS=ss(A,B,C,D), G=tf(SYS)
s=tf('s'); Gd=G*s;
% LQG from Doyle with sw=1
q=1; Q=[1 1; 1 1]; QXU = blkdiag(q*Q,1);
sw=1; QW=[1 1;1 1]; QWV = blkdiag(sw*QW,1);
KLQG = lqg(SYS,QXU,QWV); C=tf(KLQG)
%Note: The SIMC-PID is tuned for double integrating process
tauc=0.1; Kc=1/(4*tauc^2); taui=4*tauc ; taud=4*tauc ; tauf=tauc/10;
cpid = Kc*(1+1/(taui*s))*(taud*s+1)/(tauf*s+1);

## Slide 49: “Advanced control”
Would like: Feedback solutions that can be implemented with minimum need for models
“Classical advanced regulatory control“ (ARC) based on single-loop PIDs?
  YES!
  Extensively used by industry
  Problem for engineers: Lack of design methods
    Has been around since 1930’s
    But almost completely neglected by academic researchers
  Main fundamental limitation: Based on single-loop (need to choose pairing)
ARC = Advanced regulatory control

## Slide 50: QUIZ What are the three most important inventions of process control?
Hint 1: According to Sigurd Skogestad
Hint 2: All were in use around 1940
SOLUTION
PID controller, in particular, I-action
Cascade control
Ratio control
None of these are easily implemented using MPC

## Slide 51: Ratio control
Feedforward control without a model y=f(u,d)
Just process insight
Example: Food recipe
  1 part sugar
  3 parts milk
  3 parts coffee
  MIX

## Slide 52: Usually: Combine ratio (feedforward) with feedback
  Example cake baking: Use recipe (ratio control = feedforward), but a good cook adjusts the ratio to get desired result (feedback)

## Slide 53: Ratio control combined with feedback
The correct ratio setpoint is found by feedback control (VC) based on keeping the measured controlled variable y at its desired setpoint ys..
  So also here no model is needed (just data)
F1
F2
Mixing
Typical ratio control scheme (solid red lines) with outer feedback loop (dashed red lines) to set the correct ratio.
In the figure, y is viscosity, but generally it can be any intensive variable

## Slide 54: When should we use ratio control?
Answer: When fixing the ratio of all extensive variables (e.g., F2/F1) gives constant intensive variables (y).
The use of ratio control assumes the
  Scaling or scale-up property: We get the same steady-state solution if we increase all extensive variables (flows and heat rates) by the same factor compared to a basis. (Reklaitis, 1981)
For this to hold we must assume constant process efficiencies (Skogestad, 2009):
  The scaling property holds if the process efficiencies are independent of the throughput.
Similar to the use in thermodynamics, the scaling property holds for equilibrium systems. The scaling property (and thus the use of ratio control) applies to many process units, including
  Mixing
  Equilibrium reactors
  Equilibrium flash and equilibrium distillation
G.V. Reklaitis, Introduction to material & energy balances. Wiley (1983)
S. Skogestad. Chemical end energy process engineering, CRC press (2009)

## Slide 55: Cases where ratio control should not be used:
Heat exchangers (because the area is fixed during operation)
  This means, for example, that we should not fix the ratio between hot and cold flow.
  For the scaling property to hold for a heat exchanger, we would need to increase the heat transfer area A proportionally to the flow rates. This is reasonable during design but not during operation.
Non-equilibrium reactors (because the volume is fixed)
  Extent of reaction depends on kinetics and reactor volume
Compressors with varying thermodynamic efficiency
  This includes most real compressors
Mixing processes where one feed stream is fixed
Distillation with a fixed stream (e.g. heat input)

## Slide 56: Intro….
How can you control a complex plant effectively using simple elements with a minimal amount of modelling?
How can you put optimization into the control layer?
Industry has been using simple and effective as “advanced regulatory control” (ARC) schemes based on PID controllers for almost 100 years. The objective of my work is to provide a systematic approach for designing such control systems.
The main competitor to ARC is MPC (model predictive control), but the costs of implementing and maintaining MPC solutions are high. Moreover, in most cases ARC solutions (including cascade, ratio, split range and selector control) are more flexible and easier to tune. The main problem right now is that the knowledge and competence about ARC strategies is very low, especially in academia, but also in industry the knowledge is dying out. The result is that people turn off good ARC applications, simply because they don't understand what they are doing.
The reason for the lack of training and knowledge is that there has a been belief in academia since the 1980s, that ARC solutions (and PID control) are old-fashioned and will soon be replaced by MPC. However, MPC has now been around for 50 years, and yet the use of MPC is far from increasing as expected. The latest hype is that, if MPC is too complex, then machine learning is the solution. No, it is not, because or the lack of rich data (with sufficiently large input excitations) in most control applications, in particular in process control.
In summary, there is a need to change the mindset of people, both in academia and industry, People need to realize that ARC solutions should be a central part of the future. MPC of course has its place, but mainly as an improvement for large-scale applications that can afford the effort.
The talk will emphasize the above points and in addition present a systematic approach to ARC methods based on my recent paper (which is open access).
Reference: Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Published in: Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages).
Sigurd Skogestad is a Professor in chemical engineering at the Norwegian University of Science and Technology (NTNU) in Trondheim. He received his PhD from Caltrech in 1987 and he is the principal author together with Ian Postlethwaite of the book "Multivariable feedback control" published by Wiley in 1996 (first edition) and 2005 (second edition). The goal of his research is to develop simple yet rigorous methods to solve problems of engineering significance. Research interests include the use of feedback as a tool to (1) reduce uncertainty (including robust control), (2) change the system dynamics (including stabilization), and (3) generally make systema more well-behaved (including self-optimizing control). Other interests include limitations on performance in linear systems, control structure design and plantwide control, interactions between process design and control, and distillation column design, control and dynamics. His other main interests are mountain skiing (cross country), orienteering (running around with a map) and grouse hunting.

## Slide 57: ARC: Standard Advanced control elements
Each element links a subset of inputs with a subset of outputs. Results in simple local design and tuning
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Annual Reviews in Control, vol. 56 (2023), Article 100903 (44 pages).
ARC = advanced reguklatory control

## Slide 58: Common ARC elements
E1. Cascade control
Have Extra output (state) measurements
E2. Ratio control
“Feedforward” for mixing process
E12. Decoupling elements
Have interactive process
E13. Linearization elements / Adaptive gain
Have Nonlinear process
E5-E7. Split-range control (or multiple controllers or VPC)
Need extra inputs (MV) to handle all conditions (steady state) (MV-MV switching)
E3. Valve position control (VPC) (Input resetting/Midranging control)
Have extra inputs dynamically
E4. Selectors
Have changes in active constraints (CV-CV switching)
Often static nonlinear «function block»
One unifying approach is «Transformed inputs» (similar to feedback linearization)
ARC = Advanced regulatory control
VPC = Valve position control
CV = Controlled variable
MV = manipulated variable

## Slide 59: How design standard ARC elements?
Industrial literature (e.g., Shinskey).
Many nice ideas. But not systematic. Difficult to understand reasoning
Academia: Very little work
  I feel alone

## Slide 60: Constraint switching (because it is optimal at steady state)
CV-CV switching
  Control one CV at a time
  Use selectors
MV-MV switching
  Use one MV at a time
  Use split range control, split parallel control or VPC
MV-CV switching
  MV saturates so must give up CV
  Two alterntaives:
    Simple («do nothing»). If we followed input saturation rule
    Complex (repairing of loops). Need to combine MV-MV and CV-CV switching
Process
Process
Process
Process

## Slide 61: Example adaptive cruise control: CV-CV switch (min-selector) followed by MV-MV switch (split range control)

## Slide 62
p0
F0
F
p
QUIZ Compressor control
Suggest a solution which achieves
p< pmax= 37 bar (max delivery pressure)
P0 > pmin = 30 bar (min. suction pressure)
F < Fmax = 19 t/h (max. production rate)
F0 > Fmin = 10 t/h (min. through compressor
to avoid surge)
CW
p0
F0
F
p
CW
FC
PC
PC
FC
MAX
pmin=
30bar
Fmax=
19 t/h
pmax=
37bar
z
SOLUTION
All these 4 constraints are satisfied by a large z
-> MAX-selector
MAX
z
Zmin=0
MAX
z
Zmin=0
FC
Fmin=
10 t/h
Fmin=
10 t/h

## Slide 63: Cow case study (Norway, outdoor 15C to -20C)
CT
TT
Fan: u1
Heater: u2
Temperature transmitter
CO2 transmitter
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
M.Adlouni / Gemini
Disturbances:
Number of cows (they generate CO2 and heat)
  Because of heat from cows it’s always colder outside
Outdoor temperature (between 15C and -20C)
  The cows are outside in the summer

## Slide 64
CI
TI
u1
u1=50%
MAX
CC
SP=1000ppm
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
Lower CO2 (less than 1000ppm) is satisfied by large fan speed MAX-selector

## Slide 65
CI
TI
u1
u1=50%
MIN
MAX
CC
TC
SP=5C
SP=1000ppm
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
Winter: T (inside) may drop to 5C.
Control: Higher T (above 5C) is satisfied by small fan speed MIN-selector

## Slide 66
CI
TI
u1
u1=50%
MAX
CC
TC
SP=5C
SP=1000ppm
TC
SP=4C
u2
MIN
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
Winter (colder): Cannot reduce fan more because CO2 > 1000 ppm.
Start heater. Use split parallell control (could use split range control instead)

## Slide 67
CI
TI
u1
u1=50%
MAX
CC
TC
SP=5C
SP=1000ppm
TC
SP=4C
u2
TC
SP=0C
MIN
MIN
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
Winter (even colder outide): Heater at max and T drops to 0C.
To avoid freezing unhappy cows: reduce fan speed and accept CO2 > 1000 ppm
Recall: Higher T (above 0C) is satisfied by small fan speed MIN-selector

## Slide 68
CI
TI
u1
u1=50%
MAX
CC
TC
SP=5C
SP=1000ppm
TC
u2
TC
SP=0C
MIN
MIN
CC
SP=3000ppm
MAX
SP=4C
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
Winter (even colder outside): CO2 reaches unacepptable level (3000ppm)
Recall: Lower CO2 is satisfied by large fan speed MAX-selector

## Slide 69
CI
TI
u1
u1=50%
MAX
CC
TC
SP=5C
SP=1000ppm
TC
u2
TC
SP=0C
MIN
MIN
CC
SP=3000ppm
MAX
SP=4C
TC
SP=20C
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
Lower T (below 20C) is satisfied by large fan speed MAX-selector
(Consistent with large fan speed (MAX-selector) to keep CO2 < 3000ppm!)

## Slide 70
CI
TI
u1
u1=50%
MAX
CC
TC
SP=5C
SP=1000ppm
TC
u2
TC
SP=0C
MIN
MIN
CC
SP=3000ppm
MAX
SP=4C
TC
SP=20C
Happy cows
y1=C (CO2) less than 1000 ppm
y2=T between 5C and 20C
Not too much draft or noise from fan
  50% fan speed is good
Unhappy cows
y2=T less than 0C
Even more unhappy
y1=C above 3000 ppm (poor air quality)
MVs
u1=fan (cheap)
u2=heater (expensive)
FINAL OPTIMAL CONTROL STRUCTURE:
4 TCs, 2 CCs, 4 selectors
If extreme cold: Use blankets for cows
If very hot: Spray water on cows

## Slide 71: Conclusion. The future of process control
1. «Advanced regulatory control» (ARC) or «Advanced PID»:
  Works very well in many cases
  Optimization by feedback (active constraint switching)
  Need to pair input and output.
    Advantage: The engineer can specify directly the solution
    Problem: Unique pairing may not be possible for complex cases
  Need model only for parts of the process (for tuning)
  Challenge: Need better teaching and design methods
2. MPC may be better (and simpler) for some complex multivariable cases
  But combine with lower-layer PID (cascade and ratio control)
  Main challenge MPC: Need dynamic model for whole process (costly)
  Other challenge: Tuning may be difficult
(3.= Machine learning: NO, not enough relevant data )

## Slide 72
In summary, ‘‘PID control’’ researchers are recommended
to switch their attention to ‘‘advanced PID control’’, that is, the
interconnection of the PID controller with the other advanced control
elements.
Sigurd Skogestad, ''Advanced control using decomposition and simple elements''. Annual Reviews in Control, vol. 56 (2023), Article 100903

## Slide 73
Optimal centralized
Solution (EMPC)
Sigurd (me)
Academic process control community fish pond
Simple solutions that
work (ARC = PID++)
Please join me, we feel a little alone
Jose Luis

## Slide 75: NOTE
«That something works doesn’t mean that it couldn’t be much better or simpler (PID), or even both better and simpler at the same time».
Example: Sensor in wrong room
G
IT WORKS BY THE MAGIC OF FEEDBACK!
But it could be much better
y2
y1
y1
y2
y = temperature = output = controlled variable